## Manual
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
MANUAL
TABLE OF CONTENTS
| I. | Purpose
| II. | Organization
| III. | User Guide
| IV. | Notes
| V. | Disclaimer
I. PURPOSE
The purpose of the Lighting Audit & Design Tool is two-fold:
1. To document the pre- and post-installation cases of the lighting retrofit.
2. To facilitate the calculation of energy and demand reductions for large lighting installations.
II. ORGANIZATION
The Lighting Audit & Design Tool is organized into 8 sheets.
(1) Manual
FOR REFERENCE ONLY
The "Manual" sheet contains the instructions for using the Lighting Audit & Design Tool.
(2) Changelog
FOR REFERENCE ONLY
The "Changelog" sheet provides an itemized list of major changes from the previous version of the tool.
(3) Glossary
FOR REFERENCE ONLY
The "Glossary" sheet defines key inputs and outputs by column heading for all tabs accepting user inputs. This sheet should be consulted in the event that the user cannot determine what is being asked or presented in any of the fields requiring input or providing outputs.
(4) General Information
USER INPUT REQUIRED
The "General Information" sheet is where the user identifies facility-specific details of the project that have an effect on the calculation of gross savings. Facility-specific details include such things as contact information, electric utility, building area information, and operating schedule.
(5) Lighting Inventory
USER INPUT REQUIRED
The "Lighting Inventory" sheet is the main worksheet that calculates energy savings and peak demand reduction for the user-specified lighting fixture and controls improvements. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross savings for implementation and evaluation purposes. All key variable are entered on this sheet.
(6) Fixture Identities
FOR REFERENCE ONLY / USER INPUT REQUIRED FOR CUSTOM AND LED FIXTURES
The "Fixture Identities" sheet contains the master list of fixtures recognized by the Lighting Audit & Design Tool. Each allowable fixture has a unique fixture code, description, and stipulated wattage value. The sheet has filtering functions enabled so users can search for specific fixture codes by any of the associated parameters. The sheet also has input fields for custom fixture codes and non-integrated ballast LEDs that must be accompanied by cut sheets. Note that inclusion of a fixture in this table does not guarantee compliance with specific program requirements.
(7) Summary
FOR REFERENCE ONLY
The "Summary" sheet contains an overview of the customer information, the quantities of measures installed, and the associated total savings achieved by the project.
(8) Lookups
FOR REFERENCE ONLY
The "Lookups" sheet contains reference tables that are used by the tool to assign associated values to selected parameters within the sheets where user input is required.
III. USER GUIDE
1. This tool is required for projects over 20 kW of connected load savings to facilitate calculation of savings pursuant to the PA TRM. Use of this tool for projects under 20 kW should conform to EDC program rules. Consult the TRM for clarification on rules for calculating savings.
2. Begin at the "Project / Site Information" portion of the "General Information" tab, filling in all orange cells. For more detailed information on any of the requirements of the input cells available in this section, select the heading from the full list below, or use the search function in the "Glossary" tab.
G:D13 |  |  |  | Applicant Name | For cell D13, "Applicant Name", specify the name of the applicant as corroborated by the submitted W9. | Phone | For cell D20, "Phone", designate the phone number where the designated contact can be reached.
G:D14 |  |  |  | Facility Name | For cell D14, "Facility Name", specify a name of the facility in question for reference in the event that the applicant will be submitting applications for multiple facilities within one program year. | Email | For cell D21, "Email", designate the email address where the designated contact can be reached.
G:D16 |  |  |  | Address | For cell D16, "Address", specify the address at which the project takes place. | Facility Type | For cell D23, "ASHRAE Facility Type", select the option from the drop-down menu that best describes the usage of the facility.
G:D17 |  |  |  | City | For cell D17, "City", specify the city in which the facility is located. | Construction Type | For cell D24, "Construction Type", specify whether this project is for a lighting retrofit project or for new construction.
G:H17 |  |  |  | State | For cell H17, "State", specify the state in which the facility is located. | Facility Size | For cell D25, "Facility Size", specify the total square footage of the facility at which the project occurs. This field is optional for retrofit applications.
G:J17 |  |  |  | Zip | For cell J17, "Zip", specify the zip code in which the facility is located. | Installation Date | For cell I25, "Heating Fuel Type", specify whether the facility is serviced by gas or electric heat.
G:D18 |  |  |  | Utility | For cell D18, "Utility", specify the electric distribution company who services the facility. | HOU/CF Source | For cell D26, "Installation Date", specify the completion (or expected completion) date of the project.
G:H18 |  |  |  | Account No. | For cell H18, "Account No.", specify the account number on record with electric distributing company. If this is a pre-application for a new construction project, and service has not yet been connect, input "TBD". | Facility for the Visually Impaired | For cell I26, "HOU/CF Source", specify whether this project will be evaluated using TRM-deemed hours of use and coincidence factors, or if custom operating schedules will be designated.
G:D19 |  |  |  | Contact Name and Title | For cell D19, "Contact Name and Title", designate the person who should be contacted in the event that there are any questions regarding this application. | Exterior Lighting Zone
G:I27 |  |  |  | Small Business Direct Install | For cell I27, indicate whether or not this is a small business direct install project. Selecting "Yes" will disable the T12 baseline adjustment feature.
G:D20 |  |  |  | Phone | For cell D20, "Phone", designate the phone number where the designated contact can be reached.
G:D21 |  |  |  | Email | For cell D21, "Email", designate the email address where the designated contact can be reached.
G:D23 |  |  |  | ASHRAE Facility Type | For cell D23, "ASHRAE Facility Type", select the option from the drop-down menu that best describes the usage of the facility.
G:D24 |  |  |  | Construction Type | For cell D24, "Construction Type", specify whether this project is for a lighting retrofit project or for new construction.
G:D25 |  |  |  | Facility Size | For cell D25, "Facility Size", specify the total square footage of the facility at which the project occurs. This field is optional for retrofit applications.
G:D26 |  |  |  | Installation Date | For cell D26, "Installation Date", specify the completion (or expected completion) date of the project.
G:I26 |  |  |  | HOU/CF Source | For cell I26, "HOU/CF Source", specify whether this project will be evaluated using TRM-specified hours of use and coincidence factors, or if custom operating schedules will be designated.
G:I28 |  |  |  | Facility for the Visually Impaired | For cell I28, "Does this facility service the visually impaired?", specify whether this facility services people with visual impairments. This is needed to determine the appropriate ASHRAE LPD.
G:I29 |  |  |  | Exterior Lighting Zone | For cell I29, "Which exterior lighting zone describes your project?", specify the ASHRAE Exterior Lighting Zone to which this building belongs. This is needed to determine the appropriate ASHRAE minimum LPD allowance for exterior fixtures.
F:K9 |  |  |  |  | For cell K9, input the cut sheet verified wattage for the custom LED fixture.
F:F932 |  |  |  |  | For cell F932, input the description of the custom lighting fixture as corresponds to the submitted cut sheet.
F:K932 |  |  |  |  | For cell K932, input the cut sheet verified wattage of the custom fixture.
F:M932 |  |  |  |  | For cell M932, input the load shape under which the custom fixture type should be evaluated. Only screw-in LEDs and CFLs should be listed as "Screw-in". All other bulb types should be evaluated under the "General" lighting load shape.
3. Use the "Space Type Details" portion of the "General Information" tab to group fixtures into spaces with similar usages, hours of operation, and cooling type. For more detailed information on any of the requirements of the input cells available, or any of the calculated values in this section, select the heading from the full list below, or use the search function in the "Glossary" tab. When using the building area method for a new construction project that includes exterior lighting, the first row of the "Space Type Details" table should be set to a "Space Type" of NEW CONSTRUCTION WHOLE BUILDING and the second row should be set to a "Space Type" corresponding to the exterior lighting type.
G:D38 |  |  |  | Calculation Method | Cell D38, "Calculation Method", is only applicable in the event that the application is for a New Construction project. In this case, specify whether the project should be evaluated using the "Space-by-Space Method" or the "Building Area Method".
G:C42 |  |  |  | Space Designation | For cells C42 through C61, "Space Designation", provide a name for the space described in the details of subsequent columns.
G:D42 |  |  |  | Space Type | For cells D42 through D61, "Space Type", select the option from the drop-down menu that best describes the usage of the designated space type. These space types will be the only spaces available on the lighting inventory sheet, so be sure to include all spaces included in the project.
G:J42 |  |  |  | Schedule | For cells J42 through J61, "Schedule", which schedule will be used to evaluate this space type. The user can either select to use TRM-deemed values, or a custom schedule as created in the table below. Note that in the event of custom schedules, the user will need to create the custom schedules in step 4 before they are available for selection in step 3.
G:N42 |  |  |  | Cooling Type | For cells N42 through N61, "Cooling Type", select the option from the drop-down menu that best describes the cooling type of the designated space type.
G:O42 |  |  |  | Heating Fuel Type | For cells O42 through O61, "Heating Fuel Type", select the option from the drop-down menu that best describes the heating fuel type of the designated space type.
G:P42 |  |  |  | Qty. of Units | For cells P42 through P61, "Qty. of Units", specify the number of units (defined in column Q) included in the designated space type.
G:R42 |  |  |  | Units | Cells R42 through R61, "Units", display the ASHRAE designated units for calculating wattage allowance for the space type selected.
G:U42 |  |  |  | Wattage Allowance Per Unit | Cells U42 through U61, "Wattage Allowance per Unit", display the ASHRAE designated allowable wattage per the unit described in column Q for calculating wattage allowance for the space type selected.
G:O38 |  |  |  | Allowable Watts | Cell O38, "Allowable Watts", displays the ASHRAE allowable total wattage for the facility based on the space details provided.
G:X42 |  |  |  | Atrium Height | Cells X42 through X61, "Atrium Height", for atrium space types enter the height of the atrium in feet.
4. Use the "Custom Lighting Operation Schedules" portion of the "General Information" tab to create custom HOU and CF assumptions in the event that the TRM-deemed values are not a good fit. For more detailed information on any of the requirements of the input cells available, or any of the calculated values in this section, select the heading from the full list below, or use the search function in the "Glossary" tab.
G:S15 |  |  |  | Schedule Designation | For cells R15 through AD15, "Schedule Designation", specify a name for the custom schedule being designated in the cells below.
G:S17 |  |  |  | On | Each row in the "On" column represents the time at which the lights are turned on for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format.
G:T17 |  |  |  | Off | Each row in the "Off" column represents the time at which the lights are turned off for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format.
G:S27 |  |  |  | Hours of Use | Each "Hours of Use" cell calculates the annual hours of use associated with the custom schedule input in the cells above. As the formula for calculating Hours of Use in this fashion is hours*day*weeks, and (24)* (7) * (52) does NOT equal 8,760, the HOU includes an adjustment factor to appropriately annualize the usage based on this calculation method.
G:S28 |  |  |  | Coincidence Factor | Each "Coincidence Factor" cell calculates the percentage of the designated peak hours that the lights will be operational according to the custom schedule input in the cells above. Intermediate calculations for this cell can be found starting in row 57.
G:AG27 |  |  |  | Screw-In HOU | Cell AF27, "Screw-In Hours of Use", displays the TRM-deemed hours of use associated with screw-in bulbs for the building type selected.
G:AG28 |  |  |  | Screw-In CF | Cell AF28, "Screw-In CF", displays the TRM-deemed coincidence factor associated with screw-in bulbs for the building type selected.
G:AH27 |  |  |  | General HOU | Cell AG27, "General Hours of Use", displays the TRM-deemed hours of use associated with general service bulbs for the building type selected.
G:AH28 |  |  |  | General CF | Cell AG28, "General Coincidence Factor", displays the TRM-deemed coincidence factor associated with general service bulbs for the building type selected.
G:S24 |  |  |  | Holidays Observed Annually | For each "Holidays Observed Annually" cell, specify the number of days the facility shuts down completely for the given schedule.
G:S25 |  |  |  | Yearly Operating Weeks | For each "Yearly Operating Weeks" cell, specify the number of weeks the facility operates at the given custom schedule.
G:S26 |  |  |  | Unoccupied Peak Weeks | For each "Unoccupied Peak Weeks" cell, specify the number of weeks the facility is closed during the months of June, July, and August for the given custom schedule.
5. Once all information has been input into the "General Information" tab, move onto the "Lighting Inventory" tab.
|  | a) | Complete the orange cells for each line item. Each line item represents fixtures in a discrete area sharing a common baseline fixture, retrofit fixture, controls type, hours of use, coincidence factor, and space cooling type. Fixtures with different entries for any of these categories must be on separate lines. Each line entry must be definitive enough to allow verification of fixture counts in well delineated and discrete areas.
L:C1 |  | b) | For Column C, "Space Type", select the space designation previously defined on the "General Information" tab where the specified fixtures where be installed. This will auto-populate the corresponding IFenergy and IFdemand values in Columns V and W. Only space types previously defined on the "General Information" tab will be available for selection in Column C.
L:D1 |  | c) | Column D, "Space Details", is optional and can be used to differentiate different zones within previously defined space types in the event that multiple line items are present for a single space type.
L:E1 |  | d) | For Column E, "Fixture Code", input the appropriate fixture code found in the "Fixture Identities" tab that most accurately represents the pre-retrofit fixture in question. The "Fixture Identities" tab can be filtered by fixture code, lighting category, subcategory, lamp code, description, ballast type, tube length (for linear fluorescents), lamp quantity, lamp wattage, fixture wattage, code-required baseline fixture, and HOU type for easily locating the appropriate fixture. If a fixture code is not listed in the "Fixture Identities" list, custom cut sheets can be input starting at row 932 of the "Fixture Identities" sheet. Custom cut sheets must be accompanied by a manufacturer's specification sheet for wattage confirmation. Fixture code selection in Column E of the "Lighting Inventory" tab will auto-populate the corresponding Fixture Wattage, Baseline Fixture Code, and Baseline Fixture Wattage in Columns F, J, and K. Column E will not be available for input in the event that this is a new construction project.
L:G1 |  | e) | For Column G, "Fixture Qty.", input the quantity of fixtures removed. This will auto-populate the line item wattage and baseline line item wattage in Columns H and L. Column G will not be available for input in the event that this is a new construction project.
L:I1 |  | f) | For Column I, "Control Type", input the control strategy code that best describes the lighting control strategy employed prior to commencement of the project. This will auto-populate the SVGbase value in Column AC. Column I will not be available for input in the event that this is a new construction project. Controls supported by this tool include:
1. S_LS - Light Switch for Switch Strategy
2. O_OS - Occupancy Sensors for Occupancy Strategy
3. O_TC - Time Clocks for Occupancy Strategy
4. O_EMS - Energy Management System for Occupancy Strategy
5. DL_PS - Photosensors for Daylighting Strategy
6. DL_TC - Time Clocks for Daylighting Strategy
7. PT_DIM - Dimmers for Personal Tuning Strategy
8. PT_WS - Wireless on-off switches for Personal Tuning Strategy
9. PT_BLS - Bi-level switches for Personal Tuning Strategy
10. PT_CC - Computer based controls for Personal Tuning Strategy
11. PT_PSS - Pre-set scene selection for Personal Tuning Strategy
12. IT_DIM - Dimmable ballasts for Institutional Tuning Strategy
13. IT_DIM - On-off or dimmer switches for Institutional Tuning Strategy
14. MT - Multiple Types (Occupancy and personal; tuning/daylighting and other combinations)
L:M1 |  | g) | For Column M, "Fixture Code", input the appropriate fixture code found in the "Fixture Identities" tab that most accurately represents the post-retrofit fixture in question. The "Fixture Identities" tab can be filtered by fixture code, lighting category, subcategory, lamp code, description, ballast type, tube length (for linear fluorescents), lamp quantity, lamp wattage, fixture wattage, code-required baseline fixture, and HOU type for easily locating the appropriate fixture. If a fixture code is not listed in the "Fixture Identities" list, custom cut sheets can be input starting at row 922 of the "Fixture Identities" sheet. Custom cut sheets must be accompanied by a manufacturer's specification sheet for wattage confirmation. Fixture code selection in Column M of the "Lighting Inventory" tab will auto-populate the corresponding Fixture Wattage in Column P.
L:O1 |  | h) | Column O, "Fixture Tag or ID", is optional and can be used to link fixtures to invoices or fixture codes on a fixture schedule of supplemental drawings or plans.
L:Q1 |  | i) | For Column Q, "Fixture Qty.", input the quantity of fixtures installed. This will auto-populate the line item wattage in Column R.
L:S1 |  | j) | For Column S, "Control Type", input the control strategy code that best describes the lighting control strategy employed after the completion of the project. This will auto-populate the SVGbase value in Column AC.
|  | k) | Repeat steps a through j to complete each line. For further clarification on a specific field or column, please see the "Glossary" sheet or consult the TRM. If additional assistance is required, please contact the program manager.
IV. GENERAL NOTE
It is worth noting that magnetic ballasts cannot be manufactured after July 1, 2010 based on the Energy Policy and Conservation Act of 2000. This makes assumptions as to future savings and the Total Resource Cost of the retrofit unclear.
V. DISCLAIMER
This tool allows for custom entries for several fields. This document does not modify any requirements of the PA TRM. If any discrepancy between the TRM and this document exist, the TRM should be followed.
L:F1 |  |  | Column F, "Fixture Wattage", displays the TRM-deemed wattage matching the selected fixture code for the pre-retrofit fixture. This field is only available for retrofit applications.
L:H1 |  |  | Column H, "Line Item Wattage", diplays the total wattage of the pre-retrofit scenario for the full quantity of fixture presented on the corresponding line. This field is only available for retrofit applications.
L:J1 |  |  | Column J, "Fixture Code", diplays the baseline fixture code linked to the pre-retrofit fixture code to which the installed fixtures will be compared. The baseline codes for comparison are dictated by EPACT 2005 and EISA 2007 standards. This field is only available for retrofit applications.
L:K1 |  |  | For retrofit applications, Column K, "Fixture Wattage", displays the TRM-deemed wattage matching the appropriate baseline fixture code for the pre-retrofit fixture. For new construction applications, Column K, "Allowable LPD", displays the ASHRAE designated allowable LPD for the line item provided.
L:L1 |  |  | For retrofit applications, Column L, "Line Item Wattage", displays the total wattage of the baseline scenario for the full quantity of fixture presented on the corresponding line. For new construction applications, Column L, "Allowable Watts", displays the ASHRAE allowable total wattage for the line item based on the space details provided.
L:N1 |  |  | Column N, "HOU Type", displays the load shape corresponding to the fixture type selected. The load shape will be either "General Service Lighting" or "Screw-in".
L:P1 |  |  | Column P, "Fixture Wattage", displays the TRM-deemed wattage matching the selected fixture code for the as-built fixture.
L:R1 |  |  | Column R, "Line Item Wattage", displays the total wattage of the as-built scenario for the full quantity of fixture presented on the corresponding line.
L:T1 |  |  | Column T, "HOU", displays the appropriate hours of use to be used for the line item based on the fixture code and schedule inputs.
L:U1 |  |  | Column U, "CF", displays the appropriate coincidence factor to be used for the line item based on the fixture code and schedule inputs.
L:V1 |  |  | Column V, "Ifenergy", diplays the appropriate energy interactive factor to be used for the line item based on the space type and cooling details.
L:W1 |  |  | Column W, "Ifdemand", displays the appropriate demand interactive factor to be used for the line item based on the space type and cooling details.
L:X1 |  |  | Column X, "SVGbase", displays the appropriate baseline savings factor associated with pre-retrofit controls to be used for the line item based on the control type selection. For new construction, this value is a factor of the percentage of area required by code to have sensors.
L:Y1 |  |  | Column Y, "SVGee", displays the appropriate as-built savings factor associated with as-built controls to be used for the line item based on the control type selection.
L:Z1 |  |  | Column Z, "Δ Load", presents the difference in installed watts between the pre-installation and post-installation lighting scenarios separate from the change in control strategies due to the line item details.
L:AA |  |  | Column AA, "Peak Demand", presents the fraction of connected load reduction (associated with the lighting only) expected to be coincident with the PJM peak demand period due to the line item details.
L:AB |  |  | Column AB, "Energy", presents the total annual energy saved by the lighting improvement separate from the change in control strategies due to the line item details.
L:AC |  |  | Column AC, "Peak Demand", presents the fraction of connected load reduction (associated with the controls only) expected to be coincident with the PJM peak demand period due to the line item details.
L:AD |  |  | Column AD, "Energy", presents the total annual energy saved by the change in control strategies due to the line item details.
L:AE |  |  | Column AE, "Peak Demand", presents the summation of the lighting and controls peak demand savings for the line item.
L:AF |  |  | Column AF, "Energy", presents the summation of the lighting and controls energy savings for the line item.
For cell K9, input the cut sheet verified wattage for the custom LED fixture.

## Changelog
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
CHANGELOG
Version 12 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 13 (Submitted October 27, 2010. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
4) | Added Stipulated Usage Group EFLH Table in the "User Input" sheet
5) | Added new building types with corresponding EFLH and CF values
6) | Combined "Wattage Table" and "Extension Table" into one sheet (see column I of the Wattage Table)
7) | Revised fixtures codes and descriptions in Standard Wattage Table
8) | Renamed "Fixture Code Generator" to "Fixture Code Locator" and corrected some programming glitches
Version 14 (Submitted January 19, 2011. Effective June 1, 2011)
1) | In "Manual", section 7.B, the threshold was corrected to 10%, not 15%
2) | In "User Input", Table 5 was revised to reflect TRM Table 3-2
3) | In "User Input", added note to list source for Tables 3 and 5
4) | In "Glossary", added definitions for "pre-installation" and "post-installation"
5) | In "Lighting Form", the EFLH table was updated to reflect TRM Table 3-5
Version 15 (Submitted September 13, 2011 for 2012 Tentative Order)
1) | Global change, replaced all instances of EFLH with HOU
2) | In "User Input", removed old Table 5 to eliminate stipulated hours for usage groups.
3) | In "User Input", added Table 3 to allow custom SVG factor input
Version 16 (Submitted December 4, 2011 for 2012 Final Order)
1) | In "Manual", updated language regarding usage groups.
2) | In "Glossary", removed all references to the old 50 kW threshold.
3) | In "Lighting Form", updated the HOU table to reflect the 2012 TRM (Table 3-4).
4) | In "User Input", added column for custom CF for each usage group.
Version 17 (Submitted August 31, 2012 for 2013 Tentative Order)
1) | In "Lighting Form", updated HOU and CF values lookup table to reflect the 2013 TRM table.
2) | In "Lighting Form", added new building types with corresponding EFLH and CF values to reflect the 2013 TRM table.
3) | In "Lighting Form", updated Control Technologies and Savings Factors values lookup table to reflect 2013 TRM table.
4) | Revised "Manual" and "Glossary" to reflect new changes to the 2013 TRM
Version 18 (Submitted December 3, 2012 for 2013 Final Order)
1) | Revised "Manual" to reflect new changes to the 2013 TRM
Version 19 (Submitted August 29, 2013 for 2014 Tentative Order)
1) | Created "Fixtures Form" and "Controls Form" to calculate energy and peak demand savings for lighting fixtures and controls measures separately to be consistent with TRM protocols.
Created separate tabs for "Fixtures User Input" and "Controls User Input" for user input options
2) | Added new fixture codes in the "Wattage Table" (cells 157 to 178 and cells 651 to 669)
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C
Version 20 (Submitted December 05, 2013 for 2014 Final Order)
1) | Updated "Fixture Code Locator" to be compatible with Pulse-Start Metal Halide entries.
2) | Updated header fields on "Lighting Controls Form" to create autonomy between Lighting Controls and Fixture information.
3) | Revised "Fixture Code Legend" to reflect new changes to the TRM and Appendix C.
4) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C.
5) | Updated energy and peak demand savings algorithms in the Fixtures Form tab.
Version 21 (Submitted August 21, 2014 for 2015 Tentative Order)
1) | Updated Wattage Table for additional fixtures.
2) | Included LED Traffic and Pedestrian Signal Upgrades in the Prescriptive Table (values inserted in cells directly rather than pulled from "Wattage Table").
3) | Updated "Maunal" hyperlinks to match worksheet titles and made all hyperlinks functional.
4) | Cleaned up "Glossary" to ensure all cell and column references match.
Version 22 (Submitted March 16, 2015 for 2016 Tentative Order)
1) | Overhauled setup, formatting, and interface for enhanced usability.
2) | Included "key" describing which cells are available for input and which should not be changed.
3) | Updated tool to be compatible with "New Construction" as well as "Retrofit" projects.
4) | Updated tool to be compatible with custom operating schedules.
5) | Combined controls and fixtures inputs into one tab.
6) | Added functionality to compare installed fixtures to code required baseline.
7) | Revised HOU, CF, and IF assumptions to reflect new changes to the TRM.
8) | Revised "Wattage Table", now called "Fixture Identities", to reflect new changes to the TRM and Appendix C.
9) | Transformed "Glossary" into a searchable database for easier navigation.
10) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C.
Version 23 (Submitted March 10, 2017 for 2016 TRM Errata corrections)
1) | Cells R28:AD28 (Lighting Operation Schedule section) have been corrected to enable accurate coincidence factor calculations for custom schedule designations.
2) | Data validation for array Fixture Identities F9:F28 (Description) has been changed to reference Lookups V9:V15 (formerly V9:V14), where a "Custom" option was added to the array along with a corresponding Fixture Code of "C."
3) | Range Name "LED_Codes" has been extended by 1 row to include Lookups V15:X15
4) | HOU Type was converted to a user-defined field by adding Data Validation criteria to array Fixture Identities M9:M28, enabling user to select General or Screw-In (mirroring the inputs for other custom fixtures near the bottom of the Fixture Identities worksheet)
5) | Data Validation criteria for array Fixture Identities K9:K28 was changed from Whole Number to Decimal to enable non-integer fixture wattages
6) | Cell P35 on the Lookups worksheet has been changed from “Miscellaneous” to “Miscellaneous / Other”
7) | Cell P25 on Lookups has been changed to Building Type (from Control Type)
8) | Capabilities for user-defined/custom SVGbase (new construction) and SVG ee (controls) inputs have been added to the tool by appending the lookup arrays and adding a column for custom facility types to the Lighting Inventory worksheet. Data validation rules on the Lighting Inventory worksheet have been updated accordingly.
9) | Non-Integral Ballast LED Fixture Codes table (Lookups) renamed to LED Code Builder
10) | Cell D21 on Summary worksheet has been changed to sum the two cells above (lighting and controls), rather than summing only the lighting savings (note that cell E21 does not include controls because connected load is not impacted by controls).
See PA PUC Secretarial Letter Re: Technical Reference Manual 2016 errata for additional context and related TRM changes
Version 24 (Submitted June 28, 2019 for 2021 Final Order)
1) | Adjusted custom hours of use and coincidence factor module to accommodate dusk-to-dawn lighting.
2) | Made active link on "Lighting Inventory" tab to configure custom SVG values.
3) | Decremented baseline incandescent lamp wattages for non-specialty lamps to be in compliance with EISA.
4) | Corrected error in which columns J, K, and L of the "Lighting Inventory" tab did not populate for new construction projects utilizing "Whole Building Method".
5) | Added 36" and 96" linear LED options to the LED Fixture Builder. Updated "Tube Length" calculation on the "Fixture Identities" sheet to properly report lengths for 36" and 96" lamps.
6) | Expanded functionality to allow for multiple deemed space types (i.e. interior, exterior, refrigeration, and exit). This is facilitated by using either the "Deemed" or "Mixed" modes in General Information cell I26.
7) | Adjusted LPD baseline values to be consistent with IECC 2015 as sourced from https://codes.iccsafe.org/public/document/IECC2015/chapter-4-ce-commercial-energy-efficiency.
8) | Adjusted energy savings algorithm to ignore baseline SVG factor in the event that both the pre-retrofit and post-retrofit cases both employ either method of Daylighting controls. This adjustment was made in order to correct the issue through which known photocell operating hours were further discounted by the Photocell SVG factor.
9) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix C.
10) | Revised "Glossary" sheet to reflect correct name of "Fixture Identities" sheet.
11) | Revised and expanded "LED_Codes" named range to include LED Linear Fluorescent Tube Replacement "Type" in the Description. Revised "Code" for same fixtures to append Type to the end of the Code (i.e., LTA, LTB, LTC).
12) | Revised Screw-Based CFL & LED/Other General Service Lighting Exterior and Parking Garage HOU for consistency with new TRM.
13) | Revised New Construction SVG Accountability "% Req." assumptions for consistency with IECC 2015.
14) | Added "Small Business Direct Install" input on the "General Information" worksheet. When "Yes" is selected, the T12 baseline adjustment will be disabled.
15) | Added data validation to "Space Designation" on the "General Information" sheet to prevent duplicate entry.
16) | Corrected TRM-based HOU/CF/IF for street lighting "Facility Type." If "Street Lighting" is the selected facility, "Schedule" and "Cooling Type" choices are limited appropriately.
17) | Expanded "LED_Codes" to include "Troffer LED Panel"
18) | Corrected functionality for New Construction exterior lighting projects. Tool now properly populates appropriate baseline requirements.
19) | Added "Exterior, Photocell-Controlled" facility type with dusk-to-dawn operating hours.
20) | Added additional input for Atrium space types to capture atrium height. This is required to determine New Construction LPD requirement.
21) | Revised tool to require "Heating Fuel Type" at the space type-level. Tool now accommodates multiple heating fuel types within a single project.
Version 25 (Submitted October, 2020 for 2021 TRM Update Amendment)
1) | Released with TRM Order in October, 2020
2) | Re-released without change with 2021 TRM Update Amendment Final Order in February, 2021
Version 26 (Released to EDCs and EM&V Contractors following adoption of IECC 2018 on February 14, 2022)
1) | Updated LPD allowances to reflect IECC 2018 values
2) | Expanded a lookup table to generate the appropriate exterior lighting allowances when the building area method is selected for interior lighting
3) | Corrected some minor formula errors in the 'Fixture Identities' tab
Version 27 (Submitted May 2024 for 2026 TRM Tentative Order)
1) | Updated LPD values in Lookups sheet in Building Area Method and Space-by-Space LPD Option Configurator lookup tables to reflect IECC 2021 allowances
2) | Removed "Is this a Small Business Direct Install Project?" dropdown from I27 on General Information sheet and dependent formulas on Lighting Inventory sheet (column J)
3) | Removed functionality to override T12 baseline fixtures with T8 wattages
4) | Added a row for Network Lighting Controls in SVG lookup table on Lookups sheet
5) | Removed screw-based HOU and CF from Lookups sheet
6) | Added CF_w to General Service Lighting section of HOU and CF table on Lookups sheet
7) | Ensured General Service Lighting HOU and CFs reflected TRM values
8) | Added winter peak calculation formulas to Lighting Inventory sheet where applicable
9) | Deleted "HOU Type" column, which was used to designate General vs. Screw-in, in Post-Installation Details section of Lighting Inventory sheet
10) | Adjusted HOU and CF formulas by removing references to HOU Type column, only looking up the General Service Lighting HOUs and CFs
11) | Deleted "HOU Type" column from Fixture Identities sheet
12) | Added IFdemand_w column on Lighting Inventory sheet and integrated into winter peak formulas
13) | Adapted IF by Space Cooling Type and IF for Comfort Cooled Spaces by HVAC Configuration (new term) to include updated values and new variables
14) | Adapted HOU, CF, and IF by Facility Type table in Lookups sheet to include new variables for HVAC Configuration selection on General Information sheet
15) | Reconfigured interactive effects calculations to use HVAC Configuration selection on General Information sheet
16) | Added additional Intermediate CF Calculations table on General Information sheet to account for winter CF
17) | Added new row in Custom Lighting Operation Schedules table in General Information sheet to include winter CF

## Glossary
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
GLOSSARY
Not sure what to put into a certain cell? Let us help you! Search by tab name and cell number, or use the filtering function on the table below to find the cell in question.
Tab Name: |  |  | Instructions:
| General Information | G:D13 | For cell D13, "Applicant Name", specify the name of the applicant as corroborated by the submitted W9.
Cell Reference (i.e. G13):
D13
Tab |  | Cell | Field Type | Heading | Description | Availability
General Information |  | D13 | Input Field | Applicant Name | The name of the applicant as corroborated by the submitted W9. | -
General Information |  | D14 | Input Field | Facility Name | A name of the facility for reference in the event that the applicant will be submitting applications for multiple facilities within one program year. | -
General Information |  | D16 | Input Field | Address | The address at which the project takes place. | -
General Information |  | D17 | Input Field | City | The city in which the facility is located. | -
General Information |  | H17 | Input Field | State | The state in which the facility is located. | -
General Information |  | J17 | Input Field | Zip | The zip code in which the facility is located. | -
General Information |  | D18 | Input Field | Utility | The electric distribution company who services the facility. | -
General Information |  | H18 | Input Field | Account No. | The account number on record with electric distributing company. If this is a pre-application for a new construction project, and service has not yet been connect, input "TBD". | -
General Information |  | D19 | Input Field | Contact Name and Title | The person who should be contacted in the event that there are any questions regarding this application. | -
General Information |  | D20 | Input Field | Phone | The phone number where the designated contact can be reached. | -
General Information |  | D21 | Input Field | Email | The email address where the designated contact can be reached. | -
General Information |  | D23 | Input Field | Facility Type | The Facility Type that best describes the usage of the facility. | -
General Information |  | D24 | Input Field | Construction Type | The type of project, whether it is a retrofit or new construction. | -
General Information |  | D25 | Input Field | Facility Size | The total square footage of the facility at which the project occurs. This field is optional for retrofit applications. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | D26 | Input Field | Installation Date | The completion (or expected completion) date of the project. | -
General Information |  | I26 | Input Field | HOU/CF Source | The preferred source of HOU and CF assumptions. Note that if "Deemed" is selected, the calculator will assume a single designated Facilty Type for determining hours of use and coincidence factors. | -
General Information |  | I27 | Input Field | Is this a Small Business Direct Install Project? | Indicate whether or not this is a small business direct install project. Selecting "Yes" will disable the T12 baseline adjustment feature. | -
General Information |  | I29 | Input Field | Which exterior lighting zone describes your project? | The ASHRAE exterior lighting zone associated with the facility for New Construction LPD calculations. This cell is only available for input if this is a new construction project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | D38 | Input Field | Calculation Method | The ASHRAE evaluation method for New Construction projects that should be used for this project. This cell is only available for input if this is a new construction project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | C42 | Input Field | Space Designation | The user-defined name of the space that will be defined in the subsequent columns. | -
General Information |  | D42 | Input Field | Space Type | The ASHRAE Space Type that best describes the usage of the space. These space types will be the only spaces available on the lighting inventory sheet, so be sure to include all spaces included in the project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | J42 | Input Field | Schedule | The schedule that corresponds to the selected space type. Note that in the event of custom schedules, the user will need to create the custom schedules in step 5 before they are available for selection in step 4. | -
General Information |  | N42 | Input Field | Cooling Type | The type of cooling employed in the selected space type. | -
General Information |  | O42 | Input Field | Heating Fuel Type | The heating fuel source in the selected space type. | -
General Information |  | P42 | Input Field | Qty. of Units | For cells P41 through P60, "Qty. of Units", specify the number of units (described in column R) included in the designated space type. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | R42 | Calculated Value | Units | The ASHRAE designated units for which an allowable wattage is specified for the space type selected. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | U42 | Calculated Value | Wattage Allowance Per Unit | The ASHRAE designated allowable wattager per the unit specified for the space type selected. This will be used as the baseline for savings calculations in the event that this is a New Construction project. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | X42 | Input Field | Atrium Height | For atrium space types, the height of the atrium in feet. | Only if "New Construction" is selected as the construction type in Cell D24 and Space Designation is "Atrium, < 40 ft. in height" or "Atrium, >= 40 ft. in height."
General Information |  | O38 | Calculated Value | Allowable Watts | The ASHRAE allowable total wattage for the facility based on the space details provided. | Only if "New Construction" is selected as the construction type in Cell D24.
General Information |  | R15 | Input Field | Schedule Designation | The name for the custom schedule being designated in the cells below. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | R17 | Input Field | On | The time at which the lights are turned on for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S17 | Input Field | Off | The time at which the lights are turned off for the specified scheduled during the specified day of the week. The time should be entered in 24-hr. format. For overnight hours of use, add 24 to the ending time (i.e. if the facility is a restaurant that closes at 3AM, the ending time will be 27). | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S27 | Calculated Value | Hours of Use | The annual hours of use associated with the custom schedule input in the cells above. As the formula for calculating Hours of Use in this fashion is hours*day*weeks, and (24)* (7) * (52) does NOT equal 8,760, the HOU includes an adjustment factor to appropriately annualize the usage based on this calculation method. | -
General Information |  | S28 | Calculated Value | Coincidence Factor | The percentage of the designated peak hours that the lights will be operational according to the custom schedule input in the cells above. Intermediate calculations for this cell can be found starting in row 57. | -
General Information |  | AG27 | Calculated Value | Screw-In HOU | The TRM-deemed hours of use associated with screw-in bulbs for the building type selected. | -
General Information |  | AG28 | Calculated Value | Screw-In CF | The TRM-deemed coincidence factor associated with screw-in bulbs for the building type selected. | -
General Information |  | AH27 | Calculated Value | General HOU | The TRM-deemed hours of use associated with general service bulbs for the building type selected. | -
General Information |  | AH28 | Calculated Value | General CF | The TRM-deemed coincidence factor associated with general service bulbs for the building type selected. | -
General Information |  | S24 | Input Field | Holidays Observed Annually | The number of days the facility shuts down completely. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S25 | Input Field | Yearly Operating Weeks | The number of weeks the facility operates at the custom schedules provided. | Only if "Deemed" is selected as the HOU/CF Source in Cell I26.
General Information |  | S26 | Input Field | Unoccupied Peak Weeks | The number of weeks the facility is unoccupied during the months of June, July, and Augsust. | Only if "Yearly Operating Weeks" is less than 52 in Cell V28.
Lighting Inventory |  | C13 | Input Field | Space Designation | The space type previously defined on the "General Information" tab where the specified fixtures where be installed. Only space types previously defined on the "General Information" tab will be available for selection in Column C. | -
Lighting Inventory |  | D13 | Input Field | Space Details | The specified details used to delineate fixture types within the same space type. | -
Lighting Inventory |  | E13 | Input Field | Fixture Code (Pre) | The appropriate fixture code found in the "Fixture Search" tab that most accurately represents the pre-retrofit fixture in question. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | F13 | Calculated Value | Fixture Wattage (Pre) | The TRM-deemed wattage matching the selected fixture code for the pre-retrofit fixture. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | G13 | Input Field | Fixture Quantity (Pre) | The quantity of fixtures removed as part of the retrofit. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | H13 | Calculated Value | Line Item Wattage (Pre) | The total wattage of the pre-retrofit scenario for the full quantity of fixture presented on the corresponding line. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | I13 | Input Field | Control Type (Pre) | The control technology utilized in the pre-installation case. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | J13 | Calculated Value | Fixture Code (Baseline) | The code-required baseline fixture code linked to the pre-retrofit fixture code to which the installed fixtures will be compared. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | K13 | Calculated Value | Fixture Wattage (Baseline) | The TRM-deemed wattage matching the appropriate baseline fixture code for the pre-retrofit fixture. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | K13 | Calculated Value | Allowable LPD | The ASHRAE designated allowable LPD for the line item provided. This will be used as the baseline for savings calculations in the event that this is a New Construction project. | Only if "New Construction" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | L13 | Calculated Value | Line Item Wattage (Baseline) | The total wattage of the baseline scenario for the full quantity of fixture presented on the corresponding line. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | L13 | Calculated Value | Allowable Power | The ASHRAE allowable total wattage for the line item based on the space details provided. | Only if "New Construction" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | M13 | Input Field | Fixture Code (Post) | The appropriate fixture code found in the "Fixture Search" tab that most accurately represents the post-construction fixture in question. | -
Lighting Inventory |  | N13 | Calculated Value | HOU Type | The load shape corresponding to the fixture type selected. | -
Lighting Inventory |  | O13 | Input Field | Fixture Tag or ID | The fixture designation presented on either the invoices or supplemental plans. | -
Lighting Inventory |  | P13 | Calculated Value | Fixture Wattage (Post) | The TRM-deemed wattage matching the selected fixture code for the as-built fixture. | -
Lighting Inventory |  | Q13 | Input Field | Fixture Quantity. (Post) | The quantity of fixtures removed as part of the project. | -
Lighting Inventory |  | R13 | Calculated Value | Line Item Wattage (Post) | The total wattage of the as-built scenario for the full quantity of fixture presented on the corresponding line. | -
Lighting Inventory |  | S13 | Input Field | Control Type (Post) | The control technology utilized in the as-built case. | -
Lighting Inventory |  | T13 | Calculated Value | HOU | The appropriate hours of use to be used for the line item based on the fixture code and schedule inputs. | -
Lighting Inventory |  | U13 | Calculated Value | CF | The appropriate coincidence factor to be used for the line item based on the fixture code and schedule inputs. | -
Lighting Inventory |  | V13 | Calculated Value | IFenergy | The appropriate energy interactive factor to be used for the line item based on the space type and cooling details. | -
Lighting Inventory |  | W13 | Calculated Value | IFdemand | The appropriate demand interactive factor to be used for the line item based on the space type and cooling details. | -
Lighting Inventory |  | X13 | Calculated Value | SVGbase | The appropriate baseline savings factor associated with pre-retrofit controls to be used for the line item based on the control type selection. For new construction, this value is a factor of the percentage of area required by code to have sensors. | -
Lighting Inventory |  | Y13 | Calculated Value | SVGee | The appropriate as-built savings factor associated with as-built controls to be used for the line item based on the control type selection. | -
Lighting Inventory |  | Z13 | Calculated Value | Δ Load (Lighting) | The difference in installed watts between the pre-installation and post-installation lighting scenarios separate from the change in control strategies due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AA13 | Calculated Value | Peak Demand (Lighting) | The fraction of connected load reduction (associated with the lighting only) expected to be coincident with the PJM peak demand period due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AB13 | Calculated Value | Energy (Lighting) | The total annual energy saved by the lighting improvement separate from the change in control strategies due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AC13 | Calculated Value | Peak Demand (Controls) | The fraction of connected load reduction (associated with the controls only) expected to be coincident with the PJM peak demand period due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AD13 | Calculated Value | Energy (Controls) | The total annual energy saved by the change in control strategies due to the line item details. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AE13 | Calculated Value | Peak Demand (Total) | The summation of the lighting and controls peak demand savings for the line item. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | AF13 | Calculated Value | Energy (Total) | The summation of the lighting and controls energy savings for the line item. | Only if "Retrofit" is selected as the construction type in Cell D24 of the "General Information" tab.
Lighting Inventory |  | Z7 | Calculated Value | Summary: Δ Load (Lighting) | The summation of the change in connected lighting load of all line items. | -
Lighting Inventory |  | AA7 | Calculated Value | Summary: Peak Demand (Lighting) | The summation of the peak demand savings due to lighting only of all line items. | -
Lighting Inventory |  | AB7 | Calculated Value | Summary: Energy (Lighting) | The summation of the energy savings due to lighting only of all line items. | -
Lighting Inventory |  | AC7 | Calculated Value | Summary: Peak Demand (Controls) | The summation of the peak demand savings due to controls only of all line items. | -
Lighting Inventory |  | AD7 | Calculated Value | Summary: Energy (Controls) | The summation of the energy savings due to controls only of all line items. | -
Lighting Inventory |  | AE7 | Calculated Value | Summary: Peak Demand (Total) | The summation of the total peak demand savings associated with both lighting and controls upgrades for all line items. | -
Lighting Inventory |  | AF7 | Calculated Value | Summary: Energy (Total) | The summation of the total energy savings associated with both lighting and controls upgrades for all line items. | -
Fixture Identities |  | K9 | Input Field | Watts per Fixture | The cut sheet verified wattage for the custom LED fixture. | -
Fixture Identities |  | F932 | Input Field | Description | The description of the custom lighting fixture as corresponds to the submitted cut sheet. | -
Fixture Identities |  | K932 | Input Field | Watts per Fixture | The cut sheet verified wattage of the custom fixture. | -
Fixture Identities |  | M932 | Input Field | HOU Type | The load shape under which the custom fixture type should be evaluated. | -

## General Information
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
GENERAL INFORMATION
| KEY: | Input Field |  |  | Example Cell |  |  | Cell Creating Error in Calculations
|  | Calculated Value |  |  | Intermediate Calc.
❶ Project / Site Information | [7 empty] | ❷ Custom Lighting Operation Schedules
| Provide basic project information below. | [7 empty] | If you have opted to use custom HOU/CF values, you can create up to 6 custom lighting operation schedules for varying space types using the table below. Enter the on/off times of the facility lighting for each day in 24-hr. format. The first column shows an example of a facility that is open from 8AM to 5PM on weekdays, 24 hours on Saturday, and dusk-to-dawn on Sunday for reference.
Applicant Name:
Facility Name:
[10 empty] | Schedule Designation | Example |  | <Input Name> |  | <Input Name> |  | <Input Name> |  | <Input Name> |  |  | <Input Name> |  | <Input Name> |  | TRM
| Installation Address: | [9 empty] | On | Off | On | Off | On | Off | On | Off | On |  | Off | On | Off | On | Off | General
| City: |  |  | State: |  | Zip: |  | (Standard Input Example) |  | Monday | 8 | 17
| Utility: |  | Account No.: | [6 empty] | Tuesday | 8 | 17
| Contact Name & Title: | [8 empty] | Wednesday | 8 | 17
| Phone: | [8 empty] | Thursday | 8 | 17
| Email: | [8 empty] | Friday | 8 | 17
[8 empty] | (24/7 Example) |  | Saturday | 0 | 24
| Facility Type: | [6 empty] | (Dusk-to-Dawn Example) |  | Sunday | 19 | 31
| Construction Type: | [8 empty] | Holidays Observed Annually | 8
| Facility Size (ft2): | [8 empty] | Yearly Operating Weeks | 52
| Installation Date: |  |  |  | HOU/CF Source: |  |  |  |  | Summer Unoccupied Peak Weeks | 0 | [14 empty] | Interior
[10 empty] | Winter Unoccupied Peak Weeks | 0 | [14 empty] | Interior
[10 empty] | Hours of Use | 4151.5714
[10 empty] | Summer Coincidence Factor | 0.75
[10 empty] | Winter Coincidence Factor | 0.25
❸ Space Type Details | [18 empty] | Intermediate Summer CF Calculations
| Create up to 20 custom space types using the table below. These space types will be used on the "Lighting Inventory" form to describe where fixtures were installed. | [18 empty] | Custom Coincidence Factor Calculations
[23 empty] | 15 | 16 | 17 | 18
| Interior Calculation Method: | Space by Space Method | [5 empty] | Allowable Watts: | 0 | [10 empty] | Monday |  |  | 1 | 1 | 1 | 0 | Example
[15 empty] | Wattage Allowance per Unit |  |  |  |  | Tuesday |  |  | 1 | 1 | 1 | 0
| Space Designation | Space Type |  |  |  |  | Schedule | Cooling Type | HVAC Configuration | Qty. of Units |  | Units | [7 empty] | Wednesday |  |  | 1 | 1 | 1 | 0
| Example | Office - Enclosed |  |  |  |  | Example | Comfort Conditioned | Non-Electric | 20000 |  | Square Feet | [7 empty] | Thursday |  |  | 1 | 1 | 1 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 1 | 1 | 1 | 0
| <Name Your Space Type> | [18 empty] | CF_s |  |  | 0.75
| <Name Your Space Type> | [18 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
| <Name Your Space Type> | [18 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Thursday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | CF_s |  |  | 0
| <Name Your Space Type> | [18 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
| <Name Your Space Type> | [18 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Thursday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | CF_s |  |  | 0
| <Name Your Space Type> | [18 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
| <Name Your Space Type> | [18 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Thursday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | Friday |  |  | 0 | 0 | 0 | 0
| <Name Your Space Type> | [18 empty] | CF_s |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_s |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_s |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_s |  |  | 0
Intermediate Winter CF Calculations
Custom Coincidence Factor Calculations
[23 empty] | 8 | 9 | 19 | 20
[20 empty] | Monday |  |  | 0 | 1 | 0 | 0 | Example
[20 empty] | Tuesday |  |  | 0 | 1 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 1 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 1 | 0 | 0
[20 empty] | Friday |  |  | 0 | 1 | 0 | 0
[20 empty] | CF_w |  |  | 0.25
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_w |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_w |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_w |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_w |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_w |  |  | 0
[20 empty] | Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
[20 empty] | Tuesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Wednesday |  |  | 0 | 0 | 0 | 0
[20 empty] | Thursday |  |  | 0 | 0 | 0 | 0
[20 empty] | Friday |  |  | 0 | 0 | 0 | 0
[20 empty] | CF_w |  |  | 0

## Lighting Inventory
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
LIGHTING INVENTORY
[25 empty] | PROJECT SUMMARY |  | Lighting |  |  |  | Controls |  |  | Total
|  |  |  | Using Non-Integrated Ballast LED Fixtures? Click here to configure LED fixture codes. |  |  |  |  | Using Custom Cut-Sheet Fixtures? Click here to create custom fixture codes. |  |  |  | Using Custom Controls Savings Factors? Click here to create custom SVG values. | [13 empty] | Δ Load (kW) | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh) | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh) | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh)
[27 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAVINGS
|  |  |  | PRE-RETROFIT DETAILS |  |  |  |  | BASELINE DETAILS |  |  | POST-INSTALLATION DETAILS | [5 empty] | ASSUMPTIONS | [8 empty] | LIGHTING |  |  |  | CONTROLS |  |  | TOTAL
| Line Item | Space Designation | Optional Details (e.g. Room Number or Fixture Make & Model) | Fixture Code | Fixture Wattage | Fixture Quantity | Line Item Wattage | Control Type | Fixture Code | Fixture Wattage | Line Item Wattage | Fixture Code | Fixture Tag or ID (Opt.) | Fixture Wattage | Fixture Quantity | Line Item Wattage | Control Type | HOU | Summer CF, CF_s | Winter CF, CF_w | IFenergy | Ifdemand-s | Ifdemand-w | Custom NC Facility Type (optional) | SVGbase | SVGee | Δ Load (kW) | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh) | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh) | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh) | Controls Installed Counter | Lamps Removed Counter | Lamps Installed Counter
| Ex. | Example | Example | F82EHS | 227 | 10 | 2270 | S_LS | F82EHS | 227 | 2270 | F43LL | A/A1 | 93 | 10 | 930 | O_OS | 2294 | 0.48 | 0.48 | 0.04 | 0.23 | 0.23 | Custom | 0 | 0.24 | 1.34 | 0.79114 | 0.79114 | 3196.9184 | 0.13178 | 0.13178 | 532.5016 | 0.92291 | 0.92291 | 3729.42
0 | 1 | [35 empty] | 0 | 0 | 0
0 | 2 | [35 empty] | 0 | 0 | 0
0 | 3 | [35 empty] | 0 | 0 | 0
0 | 4 | [35 empty] | 0 | 0 | 0
0 | 5 | [35 empty] | 0 | 0 | 0
0 | 6 | [35 empty] | 0 | 0 | 0
0 | 7 | [35 empty] | 0 | 0 | 0
0 | 8 | [35 empty] | 0 | 0 | 0
0 | 9 | [35 empty] | 0 | 0 | 0
0 | 10 | [35 empty] | 0 | 0 | 0
0 | 11 | [35 empty] | 0 | 0 | 0
0 | 12 | [35 empty] | 0 | 0 | 0
0 | 13 | [35 empty] | 0 | 0 | 0
0 | 14 | [35 empty] | 0 | 0 | 0
0 | 15 | [35 empty] | 0 | 0 | 0
0 | 16 | [35 empty] | 0 | 0 | 0
0 | 17 | [35 empty] | 0 | 0 | 0
0 | 18 | [35 empty] | 0 | 0 | 0
0 | 19 | [35 empty] | 0 | 0 | 0
0 | 20 | [35 empty] | 0 | 0 | 0
0 | 21 | [35 empty] | 0 | 0 | 0
0 | 22 | [35 empty] | 0 | 0 | 0
0 | 23 | [35 empty] | 0 | 0 | 0
0 | 24 | [35 empty] | 0 | 0 | 0
0 | 25 | [35 empty] | 0 | 0 | 0
0 | 26 | [35 empty] | 0 | 0 | 0
0 | 27 | [35 empty] | 0 | 0 | 0
0 | 28 | [35 empty] | 0 | 0 | 0
0 | 29 | [35 empty] | 0 | 0 | 0
0 | 30 | [35 empty] | 0 | 0 | 0
0 | 31 | [35 empty] | 0 | 0 | 0
0 | 32 | [35 empty] | 0 | 0 | 0
0 | 33 | [35 empty] | 0 | 0 | 0
0 | 34 | [35 empty] | 0 | 0 | 0
0 | 35 | [35 empty] | 0 | 0 | 0
0 | 36 | [35 empty] | 0 | 0 | 0
0 | 37 | [35 empty] | 0 | 0 | 0
0 | 38 | [35 empty] | 0 | 0 | 0
0 | 39 | [35 empty] | 0 | 0 | 0
0 | 40 | [35 empty] | 0 | 0 | 0
0 | 41 | [35 empty] | 0 | 0 | 0
0 | 42 | [35 empty] | 0 | 0 | 0
0 | 43 | [35 empty] | 0 | 0 | 0
0 | 44 | [35 empty] | 0 | 0 | 0
0 | 45 | [35 empty] | 0 | 0 | 0
0 | 46 | [35 empty] | 0 | 0 | 0
0 | 47 | [35 empty] | 0 | 0 | 0
0 | 48 | [35 empty] | 0 | 0 | 0
0 | 49 | [35 empty] | 0 | 0 | 0
0 | 50 | [35 empty] | 0 | 0 | 0
0 | 51 | [35 empty] | 0 | 0 | 0
0 | 52 | [35 empty] | 0 | 0 | 0
0 | 53 | [35 empty] | 0 | 0 | 0
0 | 54 | [35 empty] | 0 | 0 | 0
0 | 55 | [35 empty] | 0 | 0 | 0
0 | 56 | [35 empty] | 0 | 0 | 0
0 | 57 | [35 empty] | 0 | 0 | 0
0 | 58 | [35 empty] | 0 | 0 | 0
0 | 59 | [35 empty] | 0 | 0 | 0
0 | 60 | [35 empty] | 0 | 0 | 0
0 | 61 | [35 empty] | 0 | 0 | 0
0 | 62 | [35 empty] | 0 | 0 | 0
0 | 63 | [35 empty] | 0 | 0 | 0
0 | 64 | [35 empty] | 0 | 0 | 0
0 | 65 | [35 empty] | 0 | 0 | 0
0 | 66 | [35 empty] | 0 | 0 | 0
0 | 67 | [35 empty] | 0 | 0 | 0
0 | 68 | [35 empty] | 0 | 0 | 0
0 | 69 | [35 empty] | 0 | 0 | 0
0 | 70 | [35 empty] | 0 | 0 | 0

## Fixture Identities
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
FIXTURE SEARCH
Use drop-down arrows in each column heading to filter by parameter. If your application contains non-integrated ballast LED fixtures, the fixtures will need to be configured starting on row 9. If your application contains custom cut-sheet accompanied fixtures, the fixtures will need to be configured starting on row 932. All custom and non-integrated ballast LED fixtures require cut sheets for fixture configuration verification.
Fixture Code | Lighting Category | Subcategory | Lamp Code | Description | Ballast | Tube Length | Lamps Per Fixture | Watts Per Lamp | Watts Per Fixture
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
Custom LED | LED | LED Fixture | LED XXW | Edit | Electronic |  | Edit | N/A | Edit
SLED2/1 | LED | LED Screw-In | LED 2W | Screw In - Light Emitting Diode Lamp, (1) 2W | Electronic |  | 1 | 2 | 2
SLED3/1 | LED | LED Screw-In | LED 3W | Screw In - Light Emitting Diode Lamp, (1) 3W | Electronic |  | 1 | 3 | 3
SLED4/1 | LED | LED Screw-In | LED 4W | Screw In - Light Emitting Diode Lamp, (1) 4W | Electronic |  | 1 | 4 | 4
SLED5/1 | LED | LED Screw-In | LED 5W | Screw In - Light Emitting Diode Lamp, (1) 5W | Electronic |  | 1 | 5 | 5
SLED6/1 | LED | LED Screw-In | LED 6W | Screw In - Light Emitting Diode Lamp, (1) 6W | Electronic |  | 1 | 6 | 6
SLED7/1 | LED | LED Screw-In | LED 7W | Screw In - Light Emitting Diode Lamp, (1) 7W | Electronic |  | 1 | 7 | 7
SLED8/1 | LED | LED Screw-In | LED 8W | Screw In - Light Emitting Diode Lamp, (1) 8W | Electronic |  | 1 | 8 | 8
SLED9/1 | LED | LED Screw-In | LED 9W | Screw In - Light Emitting Diode Lamp, (1) 9W | Electronic |  | 1 | 9 | 9
SLED10/1 | LED | LED Screw-In | LED 10W | Screw In - Light Emitting Diode Lamp, (1) 10W | Electronic |  | 1 | 10 | 10
SLED11/1 | LED | LED Screw-In | LED 11W | Screw In - Light Emitting Diode Lamp, (1) 11W | Electronic |  | 1 | 11 | 11
SLED12/1 | LED | LED Screw-In | LED 12W | Screw In - Light Emitting Diode Lamp, (1) 12W | Electronic |  | 1 | 12 | 12
SLED13/1 | LED | LED Screw-In | LED 13W | Screw In - Light Emitting Diode Lamp, (1) 13W | Electronic |  | 1 | 13 | 13
SLED14/1 | LED | LED Screw-In | LED 14W | Screw In - Light Emitting Diode Lamp, (1) 14W | Electronic |  | 1 | 14 | 14
SLED15/1 | LED | LED Screw-In | LED 15W | Screw In - Light Emitting Diode Lamp, (1) 15W | Electronic |  | 1 | 15 | 15
SLED16/1 | LED | LED Screw-In | LED 16W | Screw In - Light Emitting Diode Lamp, (1) 16W | Electronic |  | 1 | 16 | 16
SLED17/1 | LED | LED Screw-In | LED 17W | Screw In - Light Emitting Diode Lamp, (1) 17W | Electronic |  | 1 | 17 | 17
SLED18/1 | LED | LED Screw-In | LED 18W | Screw In - Light Emitting Diode Lamp, (1) 18W | Electronic |  | 1 | 18 | 18
SLED19/1 | LED | LED Screw-In | LED 19W | Screw In - Light Emitting Diode Lamp, (1) 19W | Electronic |  | 1 | 19 | 19
SLED20/1 | LED | LED Screw-In | LED 20W | Screw In - Light Emitting Diode Lamp, (1) 20W | Electronic |  | 1 | 20 | 20
SLED21/1 | LED | LED Screw-In | LED 21W | Screw In - Light Emitting Diode Lamp, (1) 21W | Electronic |  | 1 | 21 | 21
SLED22/1 | LED | LED Screw-In | LED 22W | Screw In - Light Emitting Diode Lamp, (1) 22W | Electronic |  | 1 | 22 | 22
SLED26/1 | LED | LED Screw-In | LED 26W | Screw In - Light Emitting Diode Lamp, (1) 26W | Electronic |  | 1 | 26 | 26
CF10/2D | CFL | CFL Fixture | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Mag-STD |  | 1 | 10 | 16
CF10/2D-L | CFL | CFL Fixture | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Electronic |  | 1 | 10 | 12
CF11/1 | CFL | CFL Fixture | CF11W | Compact Fluorescent, (1) 11W lamp | Mag-STD |  | 1 | 11 | 13
CF16/2D | CFL | CFL Fixture | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Mag-STD |  | 1 | 16 | 26
CF16/2D-L | CFL | CFL Fixture | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Electronic |  | 1 | 16 | 18
CF21/2D | CFL | CFL Fixture | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Mag-STD |  | 1 | 21 | 26
CF21/2D-L | CFL | CFL Fixture | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Electronic |  | 1 | 21 | 22
CF23/1 | CFL | CFL Fixture | CF23W | Compact Fluorescent, (1) 23W lamp | Mag-STD |  | 1 | 23 | 29
CF23/1-L | CFL | CFL Fixture | CF23W | Compact Fluorescent, (1) 23W lamp | Electronic |  | 1 | 23 | 25
CF28/2D | CFL | CFL Fixture | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Mag-STD |  | 1 | 28 | 35
CF28/2D-L | CFL | CFL Fixture | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Electronic |  | 1 | 28 | 28
CF38/2D | CFL | CFL Fixture | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Mag-STD |  | 1 | 38 | 46
CF38/2D-L | CFL | CFL Fixture | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Electronic |  | 1 | 38 | 36
CF42/1-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (1) 42W lamp | Electronic |  | 1 | 42 | 48
CFQ10/1 | CFL | CFL Fixture | CFQ10W | Compact Fluorescent, quad, (1) 10W lamp | Mag-STD |  | 1 | 10 | 15
CFQ13/1 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp | Mag-STD |  | 1 | 13 | 17
CFQ13/1-L | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp, BF=1.05 | Electronic |  | 1 | 13 | 15
CFQ15/1 | CFL | CFL Fixture | CFQ15W | Compact Fluorescent, quad, (1) 15W lamp | Mag-STD |  | 1 | 15 | 20
CFQ17/1 | CFL | CFL Fixture | CFQ17W | Compact Fluorescent, quad, (1) 17W lamp | Mag-STD |  | 1 | 17 | 24
CFQ18/1 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp | Mag-STD |  | 1 | 18 | 26
CFQ18/1-L | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 | Electronic |  | 1 | 18 | 20
CFQ20/1 | CFL | CFL Fixture | CFQ20W | Compact Fluorescent, quad, (1) 20W lamp | Mag-STD |  | 1 | 20 | 23
CFQ22/1 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (1) 22W lamp | Mag-STD |  | 1 | 22 | 24
CFQ25/1 | CFL | CFL Fixture | CFQ25W | Compact Fluorescent, quad, (1) 25W lamp | Mag-STD |  | 1 | 25 | 33
CFQ26/1 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp | Mag-STD |  | 1 | 26 | 33
CFQ26/1-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp, BF=0.95 | Electronic |  | 1 | 26 | 27
CFQ28/1 | CFL | CFL Fixture | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Mag-STD |  | 1 | 28 | 33
CFQ9/1 | CFL | CFL Fixture | CFQ9W | Compact Fluorescent, quad, (1) 9W lamp | Mag-STD |  | 1 | 9 | 14
CFS7/1 | CFL | CFL Fixture | CFS7W | Compact Fluorescent, spiral, (1) 7W lamp | Electronic |  | 1 | 7 | 7
CFS9/1 | CFL | CFL Fixture | CFS9W | Compact Fluorescent, spiral, (1) 9W lamp | Electronic |  | 1 | 9 | 9
CFS11/1 | CFL | CFL Fixture | CFS11W | Compact Fluorescent, spiral, (1) 11W lamp | Electronic |  | 1 | 11 | 11
CFS13/1 | CFL | CFL Fixture | CFS13W | Compact Fluorescent, spiral, (1) 13W lamp | Electronic |  | 1 | 13 | 13
CFS15/1 | CFL | CFL Fixture | CFS15W | Compact Fluorescent, spiral, (1) 15W lamp | Electronic |  | 1 | 15 | 15
CFS20/1 | CFL | CFL Fixture | CFS20W | Compact Fluorescent, spiral, (1) 20W lamp | Electronic |  | 1 | 20 | 20
CFS23/1 | CFL | CFL Fixture | CFS23W | Compact Fluorescent, spiral, (1) 23W lamp | Electronic |  | 1 | 23 | 23
CFS26/1 | CFL | CFL Fixture | CFS26W | Compact Fluorescent, spiral, (1) 26W lamp | Electronic |  | 1 | 26 | 26
CFS27/1 | CFL | CFL Fixture | CFS27W | Compact Fluorescent, spiral, (1) 27W lamp | Electronic |  | 1 | 27 | 27
CFT13/1 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Mag-STD |  | 1 | 13 | 17
CFT18/1 | CFL | CFL Fixture | CFT18W | Compact Fluorescent, long twin., (1) 18W lamp | Mag-STD |  | 1 | 18 | 24
CFT22/1 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (1) 22W lamp | Mag-STD |  | 1 | 22 | 27
CFT24/1 | CFL | CFL Fixture | CFT24W | Compact Fluorescent, long twin, (1) 24W lamp | Mag-STD |  | 1 | 24 | 32
CFT28/1 | CFL | CFL Fixture | CFT28W | Compact Fluorescent, twin, (1) 28W lamp | Mag-STD |  | 1 | 28 | 33
CFT32/1-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (1) 32W lamp | Electronic |  | 1 | 32 | 34
CFT36/1 | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long twin, (1) 36W lamp | Mag-STD |  | 1 | 36 | 51
CFT40/1 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (1) 40W lamp | Mag-STD |  | 1 | 40 | 46
CFT40/1-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (1) 40W lamp | Electronic |  | 1 | 40 | 46
CFT40/1-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Electronic |  | 1 | 40 | 43
CFT05/1 | CFL | CFL Fixture | CFT5W | Compact Fluorescent, twin, (1) 5W lamp | Mag-STD |  | 1 | 5 | 9
CFT50/1-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (1) 50W lamp | Electronic |  | 1 | 50 | 54
CFT55/1-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (1) 55W lamp | Electronic |  | 1 | 55 | 56
CFT7/1 | CFL | CFL Fixture | CFT7W | Compact Fluorescent, twin, (1) 7W lamp | Mag-STD |  | 1 | 7 | 10
CFT9/1 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (1) 9W lamp | Mag-STD |  | 1 | 9 | 11
CF11/2 | CFL | CFL Fixture | CF11W | Compact Fluorescent, (2) 11W lamp | Mag-STD |  | 2 | 11 | 26
CF42/2-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (2) 42W lamp | Electronic |  | 2 | 42 | 100
CFQ13/2 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp | Mag-STD |  | 2 | 13 | 31
CFQ13/2-L | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp, BF=1.0 | Electronic |  | 2 | 13 | 28
CFQ17/2 | CFL | CFL Fixture | CFQ17W | Compact Fluorescent, quad, (2) 17W lamp | Mag-STD |  | 2 | 17 | 48
CFQ18/2 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp | Mag-STD |  | 2 | 18 | 45
CFQ18/2-L | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp, BF=1.0 | Electronic |  | 2 | 18 | 38
CFQ20/2 | CFL | CFL Fixture | CFQ20W | Compact Fluorescent, quad, (2) 20W lamp | Mag-STD |  | 2 | 20 | 46
CFQ22/2 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (2) 22W lamp | Mag-STD |  | 2 | 22 | 48
CFQ25/2 | CFL | CFL Fixture | CFQ25W | Compact Fluorescent, quad, (2) 25W lamp | Mag-STD |  | 2 | 25 | 66
CFQ26/2 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp | Mag-STD |  | 2 | 26 | 66
CFQ26/2-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp, BF=0.95 | Electronic |  | 2 | 26 | 50
CFQ9/2 | CFL | CFL Fixture | CFQ9W | Compact Fluorescent, quad, (2) 9W lamp | Mag-STD |  | 2 | 9 | 23
CFT13/2 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (2) 13W lamp | Mag-STD |  | 2 | 13 | 31
CFT22/2 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (2) 22W lamp | Mag-STD |  | 2 | 22 | 54
CFT28/2 | CFL | CFL Fixture | CFT28W | Compact Fluorescent, twin, (2) 28W lamp | Mag-STD |  | 2 | 28 | 66
CFT32/2-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamp | Electronic |  | 2 | 32 | 62
CFT40/2 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (2) 40W lamp | Mag-STD |  | 2 | 40 | 85
CFT40/2-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (2) 40W lamp | Electronic |  | 2 | 40 | 72
CFT40/2-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (2) 40W lamp | Electronic |  | 2 | 40 | 72
CFT5/2 | CFL | CFL Fixture | CFT5W | Compact Fluorescent, twin, (2) 5W lamp | Mag-STD |  | 2 | 5 | 18
CFT50/2-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (2) 50W lamp | Electronic |  | 2 | 50 | 108
CFT55/2-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (2) 55W lamp | Electronic |  | 2 | 55 | 112
CFT7/2 | CFL | CFL Fixture | CFT7W | Compact Fluorescent, twin, (2) 7W lamp | Mag-STD |  | 2 | 7 | 21
CFT9/2 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (2) 9W lamp | Mag-STD |  | 2 | 9 | 23
CF18/3-L | CFL | CFL Fixture | CF18W | Compact Fluorescent, (3) 18W lamp | Electronic |  | 3 | 18 | 60
CF26/3-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (3) 26W lamp | Electronic |  | 3 | 26 | 82
CF32/3-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (3) 32W lamp | Electronic |  | 3 | 32 | 114
CF42/3-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (3) 42W lamp | Electronic |  | 3 | 42 | 141
CFQ13/3 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (3) 13W lamp | Mag-STD |  | 3 | 13 | 48
CFQ22/3 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (3) 22W lamp | Mag-STD |  | 3 | 22 | 72
CFQ26/3 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (3) 26W lamp | Mag-STD |  | 3 | 26 | 99
CFT13/3 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (3) 13 W lamp | Mag-STD |  | 3 | 13 | 48
CFT40/3 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (3) 40 W lamp | Mag-STD |  | 3 | 40 | 133
CFT40/3-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (3) 40W lamp | Electronic |  | 3 | 40 | 102
CFT40/3-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (3) 40W lamp | Electronic |  | 3 | 40 | 105
CFT50/3-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (3) 50W lamp | Electronic |  | 3 | 50 | 162
CFT55/3-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (3) 55W lamp | Electronic |  | 3 | 55 | 168
CFT9/3 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (3) 9W lamp | Mag-STD |  | 3 | 9 | 34
CF26/4-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (4) 26W lamp | Electronic |  | 4 | 26 | 108
CF32/4-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (4) 32W lamp | Electronic |  | 4 | 32 | 152
CF42/4-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (4) 42W lamp | Electronic |  | 4 | 42 | 188
CFQ18/4 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (4) 18W lamp | Mag-STD |  | 4 | 18 | 90
CFT22/4 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (4) 22W lamp | Mag-STD |  | 4 | 22 | 108
CFT36/4-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (4) 36W lamp | Electronic |  | 4 | 36 | 148
CFT40/4-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (4) 40W lamp | Electronic |  | 4 | 40 | 144
CFT50/4-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (4) 50W lamp | Electronic |  | 4 | 50 | 216
CFT55/4-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (4) 55W lamp | Electronic |  | 4 | 55 | 224
CFT40/5-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (5) 40W lamp | Electronic |  | 5 | 40 | 190
CFT50/5-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (5) 50W lamp | Electronic |  | 5 | 50 | 270
CFT55/5-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (5) 55W lamp | Electronic |  | 5 | 55 | 280
CF26/6-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (6) 26W lamp | Electronic |  | 6 | 26 | 162
CF32/6-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (6) 32W lamp | Electronic |  | 6 | 32 | 228
CF42/6-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (6) 42W lamp | Electronic |  | 6 | 42 | 282
CFQ26/6-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (6) 26W lamp, BF=0.95 | Electronic |  | 6 | 26 | 150
CFT32/6-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (6) 32W lamp | Electronic |  | 6 | 32 | 186
CFT36/6-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (6) 36W lamp | Electronic |  | 6 | 36 | 212
CFT36/6-L | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp | Electronic |  | 6 | 36 | 198
CFT36/6-LH | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp/ High Ballast Factor | Electronic |  | 6 | 36 | 210
CFT40/6-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (6) 40W lamp | Electronic |  | 6 | 40 | 204
CFT40/6-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp | Electronic |  | 6 | 40 | 220
CFT40/6-LH | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp/ High Ballast Factor | Electronic |  | 6 | 40 | 233
CFT50/6-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (6) 50W lamp | Electronic |  | 6 | 50 | 324
CFT55/6-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (6) 55W lamp | Electronic |  | 6 | 55 | 336
CFT55/6-L | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp | Electronic |  | 6 | 55 | 352
CFT55/6-LH | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp/ High Ballast Factor | Electronic |  | 6 | 55 | 373
CF26/8-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (8) 26W lamp | Electronic |  | 8 | 26 | 216
CF32/8-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (8) 32W lamp | Electronic |  | 8 | 32 | 304
CF42/8-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (8) 42W lamp | Electronic |  | 8 | 42 | 376
CFT36/8-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (8) 36W lamp | Electronic |  | 8 | 36 | 296
CFT36/8-L | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp | Electronic |  | 8 | 36 | 270
CFT36/8-LH | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp/ High Ballast Factor | Electronic |  | 8 | 36 | 286
CFT40/8-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (8) 40W lamp | Electronic |  | 8 | 40 | 288
CFT40/8-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp | Electronic |  | 8 | 40 | 300
CFT40/8-LH | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp/ High Ballast Factor | Electronic |  | 8 | 40 | 340
CFT50/8-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (8) 50W lamp | Electronic |  | 8 | 50 | 432
CFT55/8-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (8) 55W lamp | Electronic |  | 8 | 55 | 448
CFT55/8-L | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp | Electronic |  | 8 | 55 | 468
CFT55/8-LH | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp/ High Ballast Factor | Electronic |  | 8 | 55 | 496
CFT36/9-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (9) 36W lamp | Electronic |  | 9 | 36 | 318
CFT40/9-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (9) 40W lamp | Electronic |  | 9 | 40 | 306
CFT50/9-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (9) 50W lamp | Electronic |  | 9 | 50 | 486
CFT55/9-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (9) 55W lamp | Electronic |  | 9 | 55 | 504
CFT40/12-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (12) 40W lamp | Electronic |  | 12 | 40 | 408
CFT50/12-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (12) 50W lamp | Electronic |  | 12 | 50 | 648
CFT55/12-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (12) 55W lamp | Electronic |  | 12 | 55 | 672
CFC7/1 | CFL | CFL Screw-In | CFC7 | Compact Fluorescent, Screw-in, (1) 7W lamp | Electronic |  | 1 | 7 | 7
CFC9/1 | CFL | CFL Screw-In | CFC9 | Compact Fluorescent, Screw-in, (1) 9W lamp | Electronic |  | 1 | 9 | 9
CFC11/1 | CFL | CFL Screw-In | CFC11 | Compact Fluorescent, Screw-in, (1) 11W lamp | Electronic |  | 1 | 11 | 11
CFC12/1 | CFL | CFL Screw-In | CFC12 | Compact Fluorescent, Screw-in, (1) 12W lamp | Electronic |  | 1 | 12 | 12
CFC13/1 | CFL | CFL Screw-In | CFC13 | Compact Fluorescent, Screw-in, (1) 13W lamp | Electronic |  | 1 | 13 | 13
CFC14/1 | CFL | CFL Screw-In | CFC14 | Compact Fluorescent, Screw-in, (1) 14W lamp | Electronic |  | 1 | 14 | 14
CFC15/1 | CFL | CFL Screw-In | CFC15 | Compact Fluorescent, Screw-in, (1) 15W lamp | Electronic |  | 1 | 15 | 15
CFC16/1 | CFL | CFL Screw-In | CFC16 | Compact Fluorescent, Screw-in, (1) 16W lamp | Electronic |  | 1 | 16 | 16
CFC17/1 | CFL | CFL Screw-In | CFC17 | Compact Fluorescent, Screw-in, (1) 17W lamp | Electronic |  | 1 | 17 | 17
CFC18/1 | CFL | CFL Screw-In | CFC18 | Compact Fluorescent, Screw-in, (1) 18W lamp | Electronic |  | 1 | 18 | 18
CFC20/1 | CFL | CFL Screw-In | CFC20 | Compact Fluorescent, Screw-in, (1) 20W lamp | Electronic |  | 1 | 20 | 20
CFC23/1 | CFL | CFL Screw-In | CFC23 | Compact Fluorescent, Screw-in, (1) 23W lamp | Electronic |  | 1 | 23 | 23
CFC26/1 | CFL | CFL Screw-In | CFC26 | Compact Fluorescent, Screw-in, (1) 26W lamp | Electronic |  | 1 | 26 | 26
CFC30/1 | CFL | CFL Screw-In | CFC30 | Compact Fluorescent, Screw-in, (1) 30W lamp | Electronic |  | 1 | 30 | 30
CCFC1.5/1 | CFL | Cold Cathode CFL | CCFC1.5 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 1.5W lamp | Electronic |  | 1 | 1.5 | 1.5
CCFC3/1 | CFL | Cold Cathode CFL | CCFC3 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 3W lamp | Electronic |  | 1 | 3 | 3
CCFC5/1 | CFL | Cold Cathode CFL | CCFC5 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 5W lamp | Electronic |  | 1 | 5 | 5
CCFC8/1 | CFL | Cold Cathode CFL | CCFC8 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 8W lamp | Electronic |  | 1 | 8 | 8
F1.51LS | Linear Fluorescent | T8 Linear Fluorescent | F15T8 | Fluorescent, (1) 18" T8 lamp | Mag-STD | 12 | 1 | 15 | 19
F1.52LS | Linear Fluorescent | T8 Linear Fluorescent | F15T8 | Fluorescent, (2) 18" T8 lamp | Mag-STD | 12 | 2 | 15 | 36
F21ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 1 | 17 | 20
F21ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 24 | 1 | 17 | 17
F21ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 24 | 1 | 17 | 15
F21ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 24 | 1 | 17 | 16
F21ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 24 | 1 | 17 | 14
F21ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 1 | 17 | 15
F21ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 24 | 1 | 17 | 14
F21LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 1 | 17 | 16
F21LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 24 | 1 | 17 | 16
F21LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 24 | 1 | 17 | 17
F21LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 1 | 17 | 17
F21LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 1 | 17 | 15
F21LS | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T8 lamp, Standard Ballast | Mag-STD | 24 | 1 | 17 | 24
F22ILE | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 Instant Start lamp, Energy Saving Magnetic Ballast | Mag-ES | 24 | 2 | 17 | 45
F22ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 2 | 17 | 33
F22ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 2 | 17 | 31
F22ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 24 | 2 | 17 | 28
F22ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 24 | 2 | 17 | 29
F22LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 2 | 17 | 31
F22LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 24 | 2 | 17 | 34
F22LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 2 | 17 | 28
F23ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 3 | 17 | 47
F23ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 24 | 3 | 17 | 49
F23ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 24 | 3 | 17 | 43
F23LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 3 | 17 | 52
F23LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 3 | 17 | 41
F24ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 4 | 17 | 61
F24ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 24 | 4 | 17 | 55
F24LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 24 | 4 | 17 | 68
F24LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 24 | 4 | 17 | 57
F31ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 1 | 25 | 26
F31ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 23
F31ILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.1), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 24
F31ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 23
F31ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 36 | 1 | 25 | 22
F31ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 36 | 1 | 25 | 22
F31ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 1 | 25 | 22
F31ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 36 | 1 | 25 | 22
F31ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 1 | 25 | 28
F31ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 1 | 25 | 27
F31LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 1 | 25 | 24
F31LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 36 | 1 | 25 | 23
F31LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 36 | 1 | 25 | 24
F31LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 1 | 25 | 22
F31LL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 1 | 25 | 26
F31LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 1 | 25 | 23
F32ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 2 | 25 | 46
F32ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 2 | 25 | 44
F32ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 36 | 2 | 25 | 43
F32ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 2 | 25 | 48
F32ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 2 | 25 | 46
F32LE | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp | Mag-ES | 36 | 2 | 25 | 65
F32LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 2 | 25 | 46
F32LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 36 | 2 | 25 | 45
F32LL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 36 | 2 | 25 | 50
F32LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 2 | 25 | 42
F32LL-V | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 36 | 2 | 25 | 70
F33ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 3 | 25 | 67
F33ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 3 | 25 | 66
F33LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 3 | 25 | 72
F33LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 3 | 25 | 62
F34ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 4 | 25 | 87
F34ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 36 | 4 | 25 | 86
F34LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 36 | 4 | 25 | 89
F34LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 36 | 4 | 25 | 84
F36ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (6) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85) | Electronic | 36 | 6 | 25 | 134
F41ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 32 | 31
F41SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 30 | 28
F41SILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 30 | 27
F41SILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 30 | 27
F41SILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 30 | 26
F41SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 30 | 25
F41SILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 30 | 24
F41SILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 30 | 24
F41SILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 30 | 23
F41SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 30 | 37
F41SILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 30 | 36
F41SILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 30 | 36
F41SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 28 | 26
F41SSILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 28 | 25
F41SSILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 28 | 25
F41SSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 28 | 24
F41SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 28 | 23
F41SSILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 28 | 22
F41SSILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 28 | 22
F41SSILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 28 | 21
F41SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 28 | 33
F41SSILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 28 | 32
F41SSILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 28 | 32
F41ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 30
F41ILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 33
F41ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 26
F41ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 30
F41ILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 31
F41ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 26
F41ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 28
F41ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 26
F41ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 32 | 36
F41LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp | Mag-ES | 48 | 1 | 32 | 35
F41LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 32 | 32
F41LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 30
F41LL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 39
F41LL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 32 | 27
F41LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 31
F41LL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 33
F41LL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 32 | 25
F41LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 30
F41LL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 32 | 26
F41LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 1 | 32 | 39
F41LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 32 | 27
F41RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 1 | 25 | 22
F41RSILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 25 | 22
F41RSILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 25 | 22
F41RSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 25 | 22
F41RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 25 | 20
F41RSILL-R/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 25 | 19
F41RSILL-R/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 25 | 19
F41RSILL-R/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 25 | 19
F41RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 1 | 25 | 30
F41RSILL-H/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 25 | 30
F41RSILL-H/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 3 Lamp Ballast | Electronic | 48 | 1 | 25 | 30
F41RSILL-H/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 4 Lamp Ballast | Electronic | 48 | 1 | 25 | 29
F42ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 32 | 59
F42SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 30 | 53
F42SILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 30 | 52
F42SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 30 | 47
F42SILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 30 | 46
F42SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 48 | 2 | 30 | 72
F42SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 28 | 48
F42SSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 28 | 47
F42SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 28 | 45
F42SSILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 28 | 44
F42SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 48 | 2 | 28 | 67
F42ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 56
F42ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 51
F42ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 2 | 32 | 65
F42ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 32 | 52
F42ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 2 | 32 | 79
F42LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp | Mag-ES | 48 | 2 | 32 | 71
F42LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 32 | 60
F42LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 59
F42LL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 32 | 53
F42LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 2 | 32 | 70
F42LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 32 | 54
F42LL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 2 | 32 | 85
F42RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 2 | 25 | 43
F42RSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 25 | 43
F42RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 25 | 38
F42RSILL-R/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 25 | 38
F42RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 2 | 25 | 58
F42RSILL-H/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 4 Lamp Ballast | Electronic | 48 | 2 | 25 | 58
F43ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 32 | 89
F43SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 30 | 78
F43SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 30 | 70
F43SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 48 | 3 | 30 | 105
F43SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 28 | 72
F43SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 28 | 66
F43SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 48 | 3 | 28 | 98
F43ILL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 3 | 32 | 90
F43ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 3 | 32 | 93
F43ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 32 | 78
F43ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 3 | 32 | 112
F43LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp | Mag-ES | 48 | 3 | 32 | 110
F43LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 32 | 93
F43LL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 3 | 32 | 92
F43LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 48 | 3 | 32 | 98
F43LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 32 | 76
F43RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 3 | 25 | 65
F43RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 25 | 57
F43RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 3 | 25 | 87
F44ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 32 | 112
F44ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 48 | 4 | 32 | 151
F44SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 30 | 105
F44SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 30 | 91
F44SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 48 | 4 | 30 | 140
F44SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 28 | 96
F44SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 28 | 86
F44SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 48 | 4 | 28 | 131
F44ILL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 4 | 32 | 118
F44ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 32 | 102
F44LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp | Mag-ES | 48 | 4 | 32 | 142
F44LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 32 | 118
F44LL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 48 | 4 | 32 | 120
F44LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 32 | 105
F44ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.2) | Electronic | 48 | 4 | 32 | 144
F44RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 4 | 25 | 85
F44RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 25 | 76
F44RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 48 | 4 | 25 | 112
F45ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (5) 48", T-8 lamp, (1) 3-lamp IS ballast and (1) 2-lamp IS ballast, NLO (BF: .85-.95) | Electronic | 48 | 5 | 32 | 148
F46ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 175
F46ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, RLO (BF< .85) | Electronic | 48 | 6 | 32 | 156
F46LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 182
F46ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.2) | Electronic | 48 | 6 | 32 | 222
F46ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, VLO (BF: >1.2) | Electronic | 48 | 6 | 32 | 255
F46SIL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (6) 48", 30W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 158
F46SSIL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (6) 48", 28W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 6 | 32 | 144
F48ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 48 | 8 | 32 | 224
F48ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 8 | 32 | 204
F48LHL | Linear Fluorescent | T8 Linear Fluorescent | F48T8/HO | Fluorescent, (8) 48", T-8 HO lamp, NLO (BF: 0.95), 4 Ballasts | Electronic | 48 | 8 | 44 | 392
F410GHL | Linear Fluorescent | T8 Linear Fluorescent | F48T5/HO | Fluorescent, (10) 48", STD HO T5 lamp | Electronic | 48 | 10 | 54 | 588
F412GHL | Linear Fluorescent | T8 Linear Fluorescent | F48T5/HO | Fluorescent, (12) 48", STD HO T5 lamp | Electronic | 48 | 12 | 54 | 702
F51ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 1 | 40 | 36
F51ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 60 | 1 | 40 | 36
F51ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 60 | 1 | 40 | 35
F51ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 60 | 1 | 40 | 34
F51ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 60 | 1 | 40 | 43
F52ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 2 | 40 | 72
F52ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 60 | 2 | 40 | 67
F52ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 60 | 2 | 40 | 80
F52ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 60 | 2 | 40 | 73
F53ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 3 | 40 | 106
F53ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 60 | 3 | 40 | 108
F54ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 60 | 4 | 40 | 134
F54ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 60 | 4 | 40 | 126
F62ILHL | Linear Fluorescent | T8 Linear Fluorescent | F72T8 | Fluorescent, (2) 72", T-8 HO lamp, Instant Start Ballast | Electronic | 72 | 2 | 65 | 147
F81ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 1 | 59 | 58
F81ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 59 | 55
F81ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 59 | 49
F81ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 96 | 1 | 59 | 68
F81ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 96 | 1 | 59 | 57
F81ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 96 | 1 | 59 | 71
F81LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp | Electronic | 96 | 1 | 86 | 85
F81LHL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp, tandem wired to 2-lamp ballast | Electronic | 96 | 1 | 86 | 80
F82ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 2 | 59 | 109
F82ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 96 | 2 | 59 | 98
F82LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (2) 96", T8 HO lamp | Electronic | 96 | 2 | 86 | 160
F83ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 3 | 59 | 167
F84ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 4 | 59 | 219
F84LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (4) 96", T8 HO lamp | Electronic | 96 | 4 | 86 | 320
F86ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (6) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 6 | 59 | 328
F21GL | Linear Fluorescent | T5 Linear Fluorescent | F24T5 | Fluorescent, (1) 24", STD T5 lamp | Electronic | 24 | 1 | 14 | 18
F21GHL | Linear Fluorescent | T5 Linear Fluorescent | F24T5/HO | Fluorescent, (1) 24", STD HO T5 lamp | Electronic | 24 | 1 | 24 | 29
F22GHL | Linear Fluorescent | T5 Linear Fluorescent | F24T5/HO | Fluorescent, (2) 24", STD HO T5 lamp | Electronic | 24 | 2 | 24 | 55
F22GL | Linear Fluorescent | T5 Linear Fluorescent | F24T5 | Fluorescent, (2) 24", STD T5 lamp | Electronic | 24 | 2 | 14 | 35
F31GHL | Linear Fluorescent | T5 Linear Fluorescent | F36T5/HO | Fluorescent, (1) 36", STD HO T5 lamp | Electronic | 36 | 1 | 39 | 43
F31GL | Linear Fluorescent | T5 Linear Fluorescent | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 36 | 1 | 21 | 27
F32GHL | Linear Fluorescent | T5 Linear Fluorescent | F36T5/HO | Fluorescent, (2) 36", STD HO T5 lamp | Electronic | 36 | 2 | 39 | 85
F32SHS | Linear Fluorescent | T5 Linear Fluorescent | F36T12/HO | Fluorescent, (2) 36", HO, lamp | Mag-STD | 36 | 2 | 50 | 114
F32GL | Linear Fluorescent | T5 Linear Fluorescent | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 36 | 2 | 21 | 52
F41GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (1) 48", STD HO T5 lamp | Electronic | 48 | 1 | 54 | 59
F41GL | Linear Fluorescent | T5 Linear Fluorescent | F48T5 | Fluorescent, (1) 48", STD T5 lamp | Electronic | 48 | 1 | 28 | 32
F41GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (1) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 1 | 54 | 62
F42GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (2) 48", STD HO T5 lamp | Electronic | 48 | 2 | 54 | 117
F42GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (2) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 2 | 54 | 118
F43GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (3) 48", STD HO T5 lamp | Electronic | 48 | 3 | 54 | 177
F43GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (3) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 3 | 54 | 182
F44GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (4) 48", STD HO T5 lamp | Electronic | 48 | 4 | 54 | 234
F44GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (4) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 4 | 54 | 240
F45GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (5) 48", STD HO T5 lamp | Electronic | 48 | 5 | 54 | 294
F46GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (6) 48", STD HO T5 lamp | Electronic | 48 | 6 | 54 | 351
F46GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (6) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 48 | 6 | 54 | 364
F48GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (8) 48", STD HO T5 lamp | Electronic | 48 | 8 | 54 | 468
F51GHL | Linear Fluorescent | T5 Linear Fluorescent | F60T5/HO | Fluorescent, (1) 60", STD HO T5 lamp | Electronic | 60 | 1 | 80 | 89
F51GL | Linear Fluorescent | T5 Linear Fluorescent | F60T5 | Fluorescent, (1) 60", STD T5 lamp | Electronic | 60 | 1 | 35 | 39
F52GL | Linear Fluorescent | T5 Linear Fluorescent | F60T5 | Fluorescent, (2) 60", STD T5 lamp | Electronic | 60 | 2 | 35 | 76
F1.51SS | Linear Fluorescent | T12 Linear Fluorescent | F15T12 | Fluorescent, (1) 18" T12 lamp | Mag-STD | 12 | 1 | 15 | 19
F1.52SS | Linear Fluorescent | T12 Linear Fluorescent | F15T12 | Fluorescent, (2) 18", T12 lamp | Mag-STD | 12 | 2 | 15 | 36
F21HS | Linear Fluorescent | T12 Linear Fluorescent | F24T12/HO | Fluorescent, (1) 24", HO lamp | Mag-STD | 24 | 1 | 35 | 62
F21SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-ES | 24 | 1 | 20 | 26
F21SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-STD | 24 | 1 | 20 | 28
F22SHS | Linear Fluorescent | T12 Linear Fluorescent | F24T12/HO | Fluorescent, (2) 24", HO lamp | Mag-STD | 24 | 2 | 35 | 90
F22SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-ES | 24 | 2 | 20 | 51
F22SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-STD | 24 | 2 | 20 | 56
F23SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-ES | 24 | 3 | 20 | 77
F23SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-STD | 24 | 3 | 20 | 84
F24SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-ES | 24 | 4 | 20 | 102
F24SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-STD | 24 | 4 | 20 | 112
F26SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-ES | 24 | 6 | 20 | 153
F26SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-STD | 24 | 6 | 20 | 168
F31EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-ES | 36 | 1 | 25 | 38
F31EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-ES | 36 | 1 | 25 | 33
F31EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Electronic | 36 | 1 | 25 | 26
F31ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-STD | 36 | 1 | 25 | 42
F31ES/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-STD | 36 | 1 | 25 | 37
F31SE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-ES | 36 | 1 | 30 | 37
F31SHS | Linear Fluorescent | T12 Linear Fluorescent | F36T12/HO | Fluorescent, (1) 36", HO lamp | Mag-STD | 36 | 1 | 50 | 70
F31SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp | Electronic | 36 | 1 | 30 | 31
F31SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp | Mag-STD | 36 | 1 | 30 | 46
F31SS/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-STD | 36 | 1 | 30 | 41
F32EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-ES | 36 | 2 | 25 | 66
F32EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Electronic | 36 | 2 | 25 | 50
F32ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-STD | 36 | 2 | 25 | 73
F32SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-ES | 36 | 2 | 30 | 74
F32SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Electronic | 36 | 2 | 30 | 58
F32SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-STD | 36 | 2 | 30 | 81
F33EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-ES | 36 | 3 | 25 | 104
F33EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Electronic | 36 | 3 | 25 | 76
F33ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-STD | 36 | 3 | 25 | 115
F33SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (3) 36", STD lamp, (1) STD ballast and (1) ES ballast | Mag-ES | 36 | 3 | 30 | 120
F33SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (3) 36", STD lamp | Mag-STD | 36 | 3 | 30 | 127
F34EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (4) 36", ES lamp | Mag-ES | 36 | 4 | 25 | 132
F34EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (4) 36", ES lamp | Electronic | 36 | 4 | 25 | 100
F34SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-ES | 36 | 4 | 30 | 148
F34SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Electronic | 36 | 4 | 30 | 116
F34SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-STD | 36 | 4 | 30 | 162
F36EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (6) 36", ES lamp | Mag-ES | 36 | 6 | 25 | 198
F36SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (6) 36", STD lamp | Mag-ES | 36 | 6 | 30 | 238
F41EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-ES | 48 | 1 | 34 | 43
F41EE/D2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES | 48 | 1 | 34 | 43
F41EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp, tandem wired, 2-lamp ballast | Mag-ES | 48 | 1 | 34 | 36
F41EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (1) 48", ES HO lamp | Mag-STD | 48 | 1 | 55 | 80
F41EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 48 | 1 | 30 | 51
F41EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic | 48 | 1 | 34 | 32
F41EL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", T-12 ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 34 | 32
F41ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-STD | 48 | 1 | 34 | 50
F41EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (1) 48", VHO ES lamp | Mag-STD | 48 | 1 |  | 123
F41IAL | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic | 48 | 1 | 25 | 25
F41IAL/T2-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 2-Lamp Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 25 | 19
F41IAL/T3-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 3-Lamp Ballast, RLO (BF<0.85) | Electronic | 48 | 1 | 25 | 20
F41SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-ES | 48 | 1 | 40 | 50
F41SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (1) 48", STD HO lamp | Mag-STD | 48 | 1 | 60 | 85
F41SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 1 | 39 | 46
F41SIL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast, tandem wired | Electronic | 48 | 1 | 39 | 37
F41SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp | Mag-STD | 48 | 1 | 39 | 60
F41SIS/T2 | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, tandem to 2-lamp ballast | Mag-STD | 48 | 1 | 39 | 52
F41SL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", T-12 STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 48 | 1 | 40 | 36
F41SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-STD | 48 | 1 | 40 | 57
F41SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (1) 48", STD VHO lamp | Mag-STD | 48 | 1 | 110 | 135
F42EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-ES | 48 | 2 | 34 | 72
F42EE/D2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp, 2 Ballasts (delamped) | Mag-ES | 48 | 2 | 34 | 76
F42EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (2) 42", HO lamp (3.5' lamp) | Mag-STD | 48 | 2 | 55 | 135
F42EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (2) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 48 | 2 | 30 | 82
F42EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic | 48 | 2 | 34 | 60
F42ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-STD | 48 | 2 | 34 | 80
F42EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (2) 48", VHO ES lamp | Mag-STD | 48 | 2 |  | 210
F42IAL/T4-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start, Tandem 4-Lamp Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 25 | 40
F42IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 2 | 25 | 39
F42SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-ES | 48 | 2 | 40 | 86
F42SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (2) 48", STD HO lamp | Mag-STD | 48 | 2 | 60 | 145
F42SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (2) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 2 | 39 | 74
F42SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (2) 48", STD IS lamp | Mag-STD | 48 | 2 | 39 | 103
F42GL | Linear Fluorescent | T12 Linear Fluorescent | F48T5 | Fluorescent, (2) 48", STD T5 lamp | Electronic | 48 | 2 | 28 | 63
F42SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-STD | 48 | 2 | 40 | 94
F42SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (2) 48", STD VHO lamp | Mag-STD | 48 | 2 | 110 | 242
F43EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-ES | 48 | 3 | 34 | 115
F43EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (3) 48", ES HO lamp (3.5' lamp) | Mag-STD | 48 | 3 | 55 | 215
F43EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (3) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 48 | 3 | 30 | 133
F43EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic | 48 | 3 | 34 | 92
F43ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-STD | 48 | 3 | 34 | 130
F43EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (3) 48", VHO ES lamp | Mag-STD | 48 | 3 |  | 333
F43IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (3) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 3 | 25 | 60
F43SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-ES | 48 | 3 | 40 | 136
F43SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (3) 48", STD HO lamp | Mag-STD | 48 | 3 | 60 | 230
F43SIL | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 3 | 39 | 120
F43SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (3) 48", STD IS lamp | Mag-STD | 48 | 3 | 39 | 162
F43SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-STD | 48 | 3 | 40 | 151
F43SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (3) 48", STD VHO lamp | Mag-STD | 48 | 3 | 110 | 377
F44EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-ES | 48 | 4 | 34 | 144
F44EE/D4 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp, 4 Ballasts (delamped) | Mag-ES | 48 | 4 | 34 | 152
F44EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (4) 48", ES HO lamp | Mag-STD | 48 | 4 | 55 | 270
F44EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (4) 48" ES Instant Start lamp, Magnetic ballast | Mag-STD | 48 | 4 | 30 | 164
F44EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", T12 ES lamp, Electronic Ballast | Electronic | 48 | 4 | 34 | 120
F44ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-STD | 48 | 4 | 34 | 160
F44EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (4) 48", VHO ES lamp | Mag-STD | 48 | 4 |  | 420
F44IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (4) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 48 | 4 | 25 | 80
F44SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-ES | 48 | 4 | 40 | 172
F44SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (4) 48", STD HO lamp | Mag-STD | 48 | 4 | 60 | 290
F44SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (4) 48", STD IS lamp, Electronic ballast | Electronic | 48 | 4 | 39 | 148
F44SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (4) 48", STD IS lamp | Mag-STD | 48 | 4 | 39 | 204
F44SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-STD | 48 | 4 | 40 | 188
F44SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (4) 48", STD VHO lamp | Mag-STD | 48 | 4 | 110 | 484
F46EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-ES | 48 | 6 | 34 | 216
F46EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Electronic | 48 | 6 | 34 | 186
F46ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-STD | 48 | 6 | 34 | 236
F46EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (6) 48", ES HO lamp (3.5' lamp) | Mag-STD | 48 | 6 | 55 | 405
F46SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-ES | 48 | 6 | 40 | 258
F46SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-STD | 48 | 6 | 40 | 282
F48EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (8) 48", ES lamp | Mag-ES | 48 | 8 | 34 | 288
F48EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (8) 48", ES HO lamp (3.5' lamp) | Mag-STD | 48 | 8 | 55 | 540
F51ILHL | Linear Fluorescent | T8 Linear Fluorescent | F60T8/HO | Fluorescent, (1) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 60 | 1 | 55 | 59
F51SHE | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-ES | 60 | 1 | 75 | 88
F51SHL | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Electronic | 60 | 1 | 75 | 69
F51SHS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-STD | 60 | 1 | 75 | 92
F51SL | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (1) 60", STD lamp | Electronic | 60 | 1 | 50 | 44
F51SS | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (1) 60", STD lamp | Mag-STD | 60 | 1 | 50 | 63
F51SVS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/VHO | Fluorescent, (1) 60", VHO ES lamp | Mag-STD | 60 | 1 | 135 | 165
F52ILHL | Linear Fluorescent | T8 Linear Fluorescent | F60T8/HO | Fluorescent, (2) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 60 | 2 | 55 | 123
F52SHE | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-ES | 60 | 2 | 75 | 176
F52SHL | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Electronic | 60 | 2 | 75 | 138
F52SHS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-STD | 60 | 2 | 75 | 168
F52SL | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (2) 60", STD lamp | Electronic | 60 | 2 | 50 | 88
F52SS | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (2) 60", STD lamp | Mag-STD | 60 | 2 | 50 | 128
F52SVS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/VHO | Fluorescent, (2) 60", VHO ES lamp | Mag-STD | 60 | 2 | 135 | 310
F61ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic | 72 | 1 | 55 | 68
F61SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-ES | 72 | 1 | 55 | 76
F61SHS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (1) 72", STD HO lamp | Mag-STD | 72 | 1 | 85 | 120
F61SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-STD | 72 | 1 | 55 | 90
F61SVS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/VHO | Fluorescent, (1) 72", VHO lamp | Mag-STD | 72 | 1 | 160 | 180
F62ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp, IS electronic ballast | Electronic | 72 | 2 | 55 | 108
F62SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-ES | 72 | 2 | 55 | 122
F62SHE | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-ES | 72 | 2 | 85 | 194
F62SHS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-STD | 72 | 2 | 85 | 220
F62SL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Electronic | 72 | 2 | 55 | 108
F62SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-STD | 72 | 2 | 55 | 145
F62SVS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/VHO | Fluorescent, (2) 72", VHO lamp | Mag-STD | 72 | 2 | 160 | 330
F63ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (3) 72", STD lamp, IS electronic ballast | Electronic | 72 | 3 | 55 | 176
F63SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (3) 72", STD lamp | Mag-STD | 72 | 3 | 55 | 202
F64ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp, IS electronic ballast | Electronic | 72 | 4 | 55 | 216
F64SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-ES | 72 | 4 | 55 | 230
F64SHE | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (4) 72", STD HO lamp | Mag-ES | 72 | 4 | 85 | 388
F64SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-STD | 72 | 4 | 55 | 244
F81EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-ES | 96 | 1 | 60 | 61
F81EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-ES | 96 | 1 | 60 | 62
F81EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Electronic | 96 | 1 | 95 | 80
F81EHL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 95 | 85
F81EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 96 | 1 | 95 | 125
F81EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Electronic | 96 | 1 | 60 | 60
F81EL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 60 | 55
F81ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-STD | 96 | 1 | 60 | 83
F81ES/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-STD | 96 | 1 | 60 | 64
F81EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (1) 96", ES VHO lamp | Mag-STD | 96 | 1 | 185 | 200
F81SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-ES | 96 | 1 | 75 | 91
F81SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-ES | 96 | 1 | 110 | 132
F81SHL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 110 | 98
F81SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-STD | 96 | 1 | 110 | 145
F81SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 1 | 75 | 70
F81SL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 96 | 1 | 75 | 67
F81SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-STD | 96 | 1 | 75 | 100
F81SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (1) 96", STD VHO lamp | Mag-STD | 96 | 1 | 215 | 230
F82EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-ES | 96 | 2 | 60 | 123
F82EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-ES | 96 | 2 | 95 | 207
F82EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Electronic | 96 | 2 | 95 | 170
F82EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-STD | 96 | 2 | 95 | 227
F82EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Electronic | 96 | 2 | 60 | 110
F82ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-STD | 96 | 2 | 60 | 138
F82EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (2) 96", ES VHO lamp | Mag-STD | 96 | 2 | 185 | 390
F82SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-ES | 96 | 2 | 75 | 158
F82SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-ES | 96 | 2 | 110 | 237
F82SHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Electronic | 96 | 2 | 110 | 195
F82SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-STD | 96 | 2 | 110 | 257
F82SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 2 | 75 | 134
F82SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-STD | 96 | 2 | 75 | 173
F82SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (2) 96", STD VHO lamp | Mag-STD | 96 | 2 | 215 | 450
F83EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-ES | 96 | 3 | 60 | 210
F83EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp, (1) 2-lamp ES Ballast, (1) 1-lamp STD Ballast | Mag-ES/STD | 96 | 3 | 95 | 319
F83EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp | Mag-STD | 96 | 3 | 95 | 352
F83EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Electronic | 96 | 3 | 60 | 179
F83ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-STD | 96 | 3 | 60 | 221
F83EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (3) 96", ES VHO lamp | Mag-STD | 96 | 3 | 185 | 590
F83SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (3) 96", STD HO lamp | Mag-STD | 96 | 3 | 110 | 392
F83SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (3) 96", STD lamp | Mag-STD | 96 | 3 | 75 | 273
F83SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (3) 96", STD VHO lamp | Mag-STD | 96 | 3 | 215 | 680
F84EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-ES | 96 | 4 | 60 | 246
F84EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-ES | 96 | 4 | 95 | 414
F84EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Electronic | 96 | 4 | 95 | 340
F84EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-STD | 96 | 4 | 95 | 454
F84EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Electronic | 96 | 4 | 60 | 220
F84ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-STD | 96 | 4 | 60 | 276
F84EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (4) 96", ES VHO lamp | Mag-STD | 96 | 4 | 185 | 780
F84SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-ES | 96 | 4 | 75 | 316
F84SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-ES | 96 | 4 | 110 | 474
F84SHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Electronic | 96 | 4 | 110 | 390
F84SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-STD | 96 | 4 | 110 | 514
F84SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 96 | 4 | 75 | 268
F84SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-STD | 96 | 4 | 75 | 346
F84SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (4) 96", STD VHO lamp | Mag-STD | 96 | 4 | 215 | 900
F86EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (6) 96", ES HO lamp | Mag-STD | 96 | 6 | 95 | 721
F86EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (6) 96", ES lamp | Mag-ES | 96 | 6 | 60 | 369
F86EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (6) 96", ES lamp | Electronic | 96 | 6 | 60 | 330
F41TS | Linear Fluorescent | T10 Linear Fluorescent | F40T10 | Fluorescent, (1) 48", T-10 lamp | Mag-STD | 48 | 1 | 40 | 51
FU1EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (1) U-Tube, ES lamp | Mag-ES | 24 | 1 | 34 | 43
FU1ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic | 24 | 1 | 32 | 31
FU1LL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp | Electronic | 24 | 1 | 32 | 32
FU1LL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 24 | 1 | 31 | 27
FU2SS | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-STD | 24 | 2 | 40 | 96
FU2SE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-ES | 24 | 2 | 40 | 85
FU2EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-ES | 24 | 2 | 34 | 72
FU2ES | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-STD | 24 | 2 | 34 | 82
FU2ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 24 | 2 | 32 | 59
FU2ILL/T4 | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, tandem wired | Electronic | 24 | 2 | 32 | 56
FU2ILL/T4-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, RLO, tandem wired | Electronic | 24 | 2 | 32 | 51
FU2ILL-H | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start HLO Ballast | Electronic | 24 | 2 | 32 | 65
FU2ILL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 24 | 2 | 32 | 52
FU2LL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp | Electronic | 24 | 2 | 32 | 60
FU2LL/T2 | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Tandem 4 lamp ballast | Electronic | 24 | 2 | 32 | 59
FU2LL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 24 | 2 | 31 | 54
FU3EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (3) U-Tube, ES lamp | Mag-ES | 24 | 3 | 35 | 115
FU3ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 24 | 3 | 32 | 89
FU3ILL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 24 | 3 | 32 | 78
FC12/1 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, (1) 12" circular lamp, RS ballast | Mag-STD | 12 | 1 | 32 | 31
FC16/1 | Circular Fluorescent | Circular Fluorescent | FC16T9 | Fluorescent, (1) 16" circular lamp | Mag-STD | 16 | 1 | 40 | 35
FC20 | Circular Fluorescent | Circular Fluorescent | FC6T9 | Fluorescent, Circlite, (1) 20W lamp, Preheat ballast | Mag-STD |  | 1 | 20 | 20
FC22/1 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, Circlite, (1) 22W lamp, preheat ballast | Mag-STD |  | 1 | 22 | 20
FC22/32/1 | Circular Fluorescent | Circular Fluorescent | FC22/32T9 | Fluorescent, Circlite, (1) 22W/32W lamp, preheat ballast | Mag-STD |  | 1 | 22/32 | 58
FC32/1 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD |  | 1 | 32 | 40
FC32/40/1 | Circular Fluorescent | Circular Fluorescent | FC32/40T9 | Fluorescent, Circlite, (1) 32W/40W lamp, preheat ballast | Mag-STD |  | 1 | 32/40 | 80
FC40/1 | Circular Fluorescent | Circular Fluorescent | FC16T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD |  | 1 | 32 | 42
FC44/1 | Circular Fluorescent | Circular Fluorescent | FC44T9 | Fluorescent, Circlite, (1) 44W lamp, preheat ballast | Mag-STD |  | 1 | 44 | 46
FC6/1 | Circular Fluorescent | Circular Fluorescent | FC6T9 | Fluorescent, (1) 6" circular lamp, RS ballast | Mag-STD | 6 | 1 | 20 | 25
FC8/1 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, (1) 8" circular lamp, RS ballast | Mag-STD | 8 | 1 | 22 | 26
FC12/2 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, (2) 12" circular lamp, RS ballast | Mag-STD | 12 | 2 | 32 | 62
FC8/2 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, (2) 8" circular lamp, RS ballast | Mag-STD | 8 | 2 | 22 | 52
F40EE/D1 | Delamp | Delamp | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (1) hot ballast | Mag-ES |  | 0 | 0 | 4
F40EE/D2 | Delamp | Delamp | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (2) hot ballast | Mag-ES |  | 0 | 0 | 8
ECF5/1 | Exit Sign | Exit Sign | CFT5W | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD |  | 1 | 5 | 9
ECF7/1 | Exit Sign | Exit Sign | CFT7W | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD |  | 1 | 7 | 10
ECF8/1 | Exit Sign | Exit Sign | F8T5 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD |  | 1 | 8 | 12
ECF9/1 | Exit Sign | Exit Sign | CFT9W | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD |  | 1 | 9 | 12
EI15/1 | Exit Sign | Exit Sign | I15 | EXIT Incandescent, (1) 15W lamp |  |  | 1 | 15 | 15
EI20/1 | Exit Sign | Exit Sign | I20 | EXIT Incandescent, (1) 20W lamp |  |  | 1 | 20 | 20
EI25/1 | Exit Sign | Exit Sign | I25 | EXIT Incandescent, (1) 25W lamp |  |  | 1 | 25 | 25
EI34/1 | Exit Sign | Exit Sign | I34 | EXIT Incandescent, (1) 34W lamp |  |  | 1 | 34 | 34
EI40/1 | Exit Sign | Exit Sign | I40 | EXIT Incandescent, (1) 40W lamp |  |  | 1 | 40 | 40
EI5/1 | Exit Sign | Exit Sign | I5 | EXIT Incandescent, (1) 5W lamp |  |  | 1 | 5 | 5
EI7.5/1 | Exit Sign | Exit Sign | I7.5 | EXIT Tungsten, (1) 7.5 W lamp |  |  | 1 | 7.5 | 8
ELED0.5/1 | Exit Sign | Exit Sign | LED0.5W | EXIT Light Emitting Diode, (1) 0.5W lamp, Single Sided |  |  | 1 | 0.5 | 0.5
ELED1.5/1 | Exit Sign | Exit Sign | LED1.5W | EXIT Light Emitting Diode, (1) 1.5W lamp, Single Sided |  |  | 1 | 1.5 | 1.5
ELED10.5/1 | Exit Sign | Exit Sign | LED10.5W | EXIT Light Emitting Diode, (1) 10.5W lamp, Single Sided |  |  | 1 | 10.5 | 10.5
ELED2/1 | Exit Sign | Exit Sign | LED2W | EXIT Light Emitting Diode, (1) 2W lamp, Single Sided |  |  | 1 | 2 | 2
ELED3/1 | Exit Sign | Exit Sign | LED3W | EXIT Light Emitting Diode, (1) 3W lamp, Single Sided |  |  | 1 | 3 | 3
ELED5/1 | Exit Sign | Exit Sign | LED5W | EXIT Light Emitting Diode, (1) 5W lamp, Single Sided |  |  | 1 | 5 | 5
ELED8/1 | Exit Sign | Exit Sign | LED8W | EXIT Light Emitting Diode, (1) 8W lamp, Single Sided |  |  | 1 | 8 | 8
ECF5/2 | Exit Sign | Exit Sign | CFT5W | EXIT Compact Fluorescent, (2) 5W lamp | Mag-STD |  | 2 | 5 | 20
ECF7/2 | Exit Sign | Exit Sign | CFT7W | EXIT Compact Fluorescent, (2) 7W lamp | Mag-STD |  | 2 | 7 | 21
ECF8/2 | Exit Sign | Exit Sign | F8T5 | EXIT T5 Fluorescent, (2) 8W lamp | Mag-STD |  | 2 | 8 | 24
ECF9/2 | Exit Sign | Exit Sign | CFT9W | EXIT Compact Fluorescent, (2) 9W lamp | Mag-STD |  | 2 | 9 | 20
EI10/2 | Exit Sign | Exit Sign | I10 | EXIT Incandescent, (2) 10W lamp |  |  | 2 | 10 | 20
EI15/2 | Exit Sign | Exit Sign | I15 | EXIT Incandescent, (2) 15W lamp |  |  | 2 | 15 | 30
EI20/2 | Exit Sign | Exit Sign | I20 | EXIT Incandescent, (2) 20W lamp |  |  | 2 | 20 | 40
EI25/2 | Exit Sign | Exit Sign | I25 | EXIT Incandescent, (2) 25W lamp |  |  | 2 | 25 | 50
EI34/2 | Exit Sign | Exit Sign | I34 | EXIT Incandescent, (2) 34W lamp |  |  | 2 | 34 | 68
EI40/2 | Exit Sign | Exit Sign | I40 | EXIT Incandescent, (2) 40W lamp |  |  | 2 | 40 | 80
EI5/2 | Exit Sign | Exit Sign | I5 | EXIT Incandescent, (2) 5W lamp |  |  | 2 | 5 | 10
EI50/2 | Exit Sign | Exit Sign | I50 | EXIT Incandescent, (2) 50W lamp |  |  | 2 | 50 | 100
EI7.5/2 | Exit Sign | Exit Sign | I7.5 | EXIT Tungsten, (2) 7.5 W lamp |  |  | 2 | 7.5 | 15
ELED0.5/2 | Exit Sign | Exit Sign | LED0.5W | EXIT Light Emitting Diode, (2) 0.5W lamp, Dual Sided |  |  | 2 | 0.5 | 1
ELED1.5/2 | Exit Sign | Exit Sign | LED1.5W | EXIT Light Emitting Diode, (2) 1.5W lamp, Dual Sided |  |  | 2 | 1.5 | 3
ELED10.5/2 | Exit Sign | Exit Sign | LED10.5W | EXIT Light Emitting Diode, (2) 10.5W lamp, Dual Sided |  |  | 2 | 10.5 | 21
ELED2/2 | Exit Sign | Exit Sign | LED2W | EXIT Light Emitting Diode, (2) 2W lamp, Dual Sided |  |  | 2 | 2 | 4
ELED3/2 | Exit Sign | Exit Sign | LED3W | EXIT Light Emitting Diode, (2) 3W lamp, Dual Sided |  |  | 2 | 3 | 6
ELED5/2 | Exit Sign | Exit Sign | LED5W | EXIT Light Emitting Diode, (2) 5W lamp, Dual Sided |  |  | 2 | 5 | 10
ELED8/2 | Exit Sign | Exit Sign | LED8W | EXIT Light Emitting Diode, (2) 8W lamp, Dual Sided |  |  | 2 | 8 | 16
I100/1 | Incandescent | Standard Incandescent | I100 | Incandescent, (1) 100W lamp |  |  | 1 | 100 | 100
I1000/1 | Incandescent | Standard Incandescent | I1000 | Incandescent, (1) 1000W lamp |  |  | 1 | 1000 | 1000
I100E/1 | Incandescent | Standard Incandescent | I100/ES | Incandescent, (1) 100W ES lamp |  |  | 1 | 90 | 90
I100EL/1 | Incandescent | Standard Incandescent | I100/ES/LL | Incandescent, (1) 100W ES/LL lamp |  |  | 1 | 90 | 90
I120/1 | Incandescent | Standard Incandescent | I120 | Incandescent, (1) 120W lamp |  |  | 1 | 120 | 120
I125/1 | Incandescent | Standard Incandescent | I125 | Incandescent, (1) 125W lamp |  |  | 1 | 125 | 125
I135/1 | Incandescent | Standard Incandescent | I135 | Incandescent, (1) 135W lamp |  |  | 1 | 135 | 135
I15/1 | Incandescent | Standard Incandescent | I15 | Incandescent, (1) 15W lamp |  |  | 1 | 15 | 15
I150/1 | Incandescent | Standard Incandescent | I150 | Incandescent, (1) 150W lamp |  |  | 1 | 150 | 150
I1500/1 | Incandescent | Standard Incandescent | I1500 | Incandescent, (1) 1500W lamp |  |  | 1 | 1500 | 1500
I150E/1 | Incandescent | Standard Incandescent | I150/ES | Incandescent, (1) 150W ES lamp |  |  | 1 | 135 | 135
I150EL/1 | Incandescent | Standard Incandescent | I150/ES/LL | Incandescent, (1) 150W ES/LL lamp |  |  | 1 | 135 | 135
I170/1 | Incandescent | Standard Incandescent | I170 | Incandescent, (1) 170W lamp |  |  | 1 | 170 | 170
I20/1 | Incandescent | Standard Incandescent | I20 | Incandescent, (1) 20W lamp |  |  | 1 | 20 | 20
I200/1 | Incandescent | Standard Incandescent | I200 | Incandescent, (1) 200W lamp |  |  | 1 | 200 | 200
I2000/1 | Incandescent | Standard Incandescent | I2000 | Incandescent, (1) 2000W lamp |  |  | 1 | 2000 | 2000
I200L/1 | Incandescent | Standard Incandescent | I200/LL | Incandescent, (1) 200W LL lamp |  |  | 1 | 200 | 200
I25/1 | Incandescent | Standard Incandescent | I25 | Incandescent, (1) 25W lamp |  |  | 1 | 25 | 25
I250/1 | Incandescent | Standard Incandescent | I250 | Incandescent, (1) 250W lamp |  |  | 1 | 250 | 250
I300/1 | Incandescent | Standard Incandescent | I300 | Incandescent, (1) 300W lamp |  |  | 1 | 300 | 300
I34/1 | Incandescent | Standard Incandescent | I34 | Incandescent, (1) 34W lamp |  |  | 1 | 34 | 34
I36/1 | Incandescent | Standard Incandescent | I36 | Incandescent, (1) 36W lamp |  |  | 1 | 36 | 36
I40/1 | Incandescent | Standard Incandescent | I40 | Incandescent, (1) 40W lamp |  |  | 1 | 40 | 40
I400/1 | Incandescent | Standard Incandescent | I400 | Incandescent, (1) 400W lamp |  |  | 1 | 400 | 400
I40E/1 | Incandescent | Standard Incandescent | I40/ES | Incandescent, (1) 40W ES lamp |  |  | 1 | 34 | 34
I40EL/1 | Incandescent | Standard Incandescent | I40/ES/LL | Incandescent, (1) 40W ES/LL lamp |  |  | 1 | 34 | 34
I42/1 | Incandescent | Standard Incandescent | I42 | Incandescent, (1) 42W lamp |  |  | 1 | 42 | 42
I448/1 | Incandescent | Standard Incandescent | I448 | Incandescent, (1) 448W lamp |  |  | 1 | 448 | 448
I45/1 | Incandescent | Standard Incandescent | I45 | Incandescent, (1) 45W lamp |  |  | 1 | 45 | 45
I50/1 | Incandescent | Standard Incandescent | I50 | Incandescent, (1) 50W lamp |  |  | 1 | 50 | 50
I500/1 | Incandescent | Standard Incandescent | I500 | Incandescent, (1) 500W lamp |  |  | 1 | 500 | 500
I52/1 | Incandescent | Standard Incandescent | I52 | Incandescent, (1) 52W lamp |  |  | 1 | 52 | 52
I54/1 | Incandescent | Standard Incandescent | I54 | Incandescent, (1) 54W lamp |  |  | 1 | 54 | 54
I55/1 | Incandescent | Standard Incandescent | I55 | Incandescent, (1) 55W lamp |  |  | 1 | 55 | 55
I60/1 | Incandescent | Standard Incandescent | I60 | Incandescent, (1) 60W lamp |  |  | 1 | 60 | 60
I60E/1 | Incandescent | Standard Incandescent | I60/ES | Incandescent, (1) 60W ES lamp |  |  | 1 | 52 | 52
I60EL/1 | Incandescent | Standard Incandescent | I60/ES/LL | Incandescent, (1) 60W ES/LL lamp |  |  | 1 | 52 | 52
I65/1 | Incandescent | Standard Incandescent | I65 | Incandescent, (1) 65W lamp |  |  | 1 | 65 | 65
I67/1 | Incandescent | Standard Incandescent | I67 | Incandescent, (1) 67W lamp |  |  | 1 | 67 | 67
I69/1 | Incandescent | Standard Incandescent | I69 | Incandescent, (1) 69W lamp |  |  | 1 | 69 | 69
I7.5/1 | Incandescent | Standard Incandescent | I7.5 | Tungsten exit light, (1) 7.5 W lamp, used in night light application |  |  | 1 | 7.5 | 8
I72/1 | Incandescent | Standard Incandescent | I72 | Incandescent, (1) 72W lamp |  |  | 1 | 72 | 72
I75/1 | Incandescent | Standard Incandescent | I75 | Incandescent, (1) 75W lamp |  |  | 1 | 75 | 75
I750/1 | Incandescent | Standard Incandescent | I750 | Incandescent, (1) 750W lamp |  |  | 1 | 750 | 750
I75E/1 | Incandescent | Standard Incandescent | I75/ES | Incandescent, (1) 75W ES lamp |  |  | 1 | 67 | 67
I75EL/1 | Incandescent | Standard Incandescent | I75/ES/LL | Incandescent, (1) 75W ES/LL lamp |  |  | 1 | 67 | 67
I80/1 | Incandescent | Standard Incandescent | I80 | Incandescent, (1) 80W lamp |  |  | 1 | 80 | 80
I85/1 | Incandescent | Standard Incandescent | I85 | Incandescent, (1) 85W lamp |  |  | 1 | 85 | 85
I90/1 | Incandescent | Standard Incandescent | I90 | Incandescent, (1) 90W lamp |  |  | 1 | 90 | 90
I93/1 | Incandescent | Standard Incandescent | I93 | Incandescent, (1) 93W lamp |  |  | 1 | 93 | 93
I95/1 | Incandescent | Standard Incandescent | I95 | Incandescent, (1) 95W lamp |  |  | 1 | 95 | 95
I100/2 | Incandescent | Standard Incandescent | I100 | Incandescent, (2) 100W lamp |  |  | 2 | 100 | 200
I120/2 | Incandescent | Standard Incandescent | I120 | Incandescent, (2) 120W lamp |  |  | 2 | 120 | 240
I135/2 | Incandescent | Standard Incandescent | I135 | Incandescent, (2) 135W lamp |  |  | 2 | 135 | 270
I15/2 | Incandescent | Standard Incandescent | I15 | Incandescent, (2) 15W lamp |  |  | 2 | 15 | 30
I150/2 | Incandescent | Standard Incandescent | I150 | Incandescent, (2) 150W lamp |  |  | 2 | 150 | 300
I20/2 | Incandescent | Standard Incandescent | I20 | Incandescent, (2) 20W lamp |  |  | 2 | 20 | 40
I200/2 | Incandescent | Standard Incandescent | I200 | Incandescent, (2) 200W lamp |  |  | 2 | 200 | 400
I25/2 | Incandescent | Standard Incandescent | I25 | Incandescent, (2) 25W lamp |  |  | 2 | 25 | 50
I34/2 | Incandescent | Standard Incandescent | I34 | Incandescent, (2) 34W lamp |  |  | 2 | 34 | 68
I40/2 | Incandescent | Standard Incandescent | I40 | Incandescent, (2) 40W lamp |  |  | 2 | 40 | 80
I50/2 | Incandescent | Standard Incandescent | I50 | Incandescent, (2) 50W lamp |  |  | 2 | 50 | 100
I52/2 | Incandescent | Standard Incandescent | I52 | Incandescent, (2) 52W lamp |  |  | 2 | 52 | 104
I54/2 | Incandescent | Standard Incandescent | I54 | Incandescent, (2) 54W lamp |  |  | 2 | 54 | 108
I55/2 | Incandescent | Standard Incandescent | I55 | Incandescent, (2) 55W lamp |  |  | 2 | 55 | 110
I60/2 | Incandescent | Standard Incandescent | I60 | Incandescent, (2) 60W lamp |  |  | 2 | 60 | 120
I65/2 | Incandescent | Standard Incandescent | I65 | Incandescent, (2) 65W lamp |  |  | 2 | 65 | 130
I67/2 | Incandescent | Standard Incandescent | I67 | Incandescent, (2) 67W lamp |  |  | 2 | 67 | 134
I7.5/2 | Incandescent | Standard Incandescent | I7.5 | Tungsten exit light, (2) 7.5 W lamp, used in night light application |  |  | 2 | 7.5 | 15
I75/2 | Incandescent | Standard Incandescent | I75 | Incandescent, (2) 75W lamp |  |  | 2 | 75 | 150
I90/2 | Incandescent | Standard Incandescent | I90 | Incandescent, (2) 90W lamp |  |  | 2 | 90 | 180
I95/2 | Incandescent | Standard Incandescent | I95 | Incandescent, (2) 95W lamp |  |  | 2 | 95 | 190
I100/3 | Incandescent | Standard Incandescent | I100 | Incandescent, (3) 100W lamp |  |  | 3 | 100 | 300
I60/3 | Incandescent | Standard Incandescent | I60 | Incandescent, (3) 60W lamp |  |  | 3 | 60 | 180
I67/3 | Incandescent | Standard Incandescent | I67 | Incandescent, (3) 67W lamp |  |  | 3 | 67 | 201
I75/3 | Incandescent | Standard Incandescent | I75 | Incandescent, (3) 75W lamp |  |  | 3 | 75 | 225
I90/3 | Incandescent | Standard Incandescent | I90 | Incandescent, (3) 90W lamp |  |  | 3 | 90 | 270
I100/4 | Incandescent | Standard Incandescent | I100 | Incandescent, (4) 100W lamp |  |  | 4 | 100 | 400
I25/4 | Incandescent | Standard Incandescent | I25 | Incandescent, (4) 25W lamp |  |  | 4 | 25 | 100
I60/4 | Incandescent | Standard Incandescent | I60 | Incandescent, (4) 60W lamp |  |  | 4 | 60 | 240
I75/4 | Incandescent | Standard Incandescent | I75 | Incandescent, (4) 75W lamp |  |  | 4 | 75 | 300
I100/5 | Incandescent | Standard Incandescent | I100 | Incandescent, (5) 100W lamp |  |  | 5 | 100 | 500
I60/5 | Incandescent | Standard Incandescent | I60 | Incandescent, (5) 60W lamp |  |  | 5 | 60 | 300
H100/1 | Incandescent | Halogen Incandescent | H100 | Halogen Incandescent, (1) 100W lamp |  |  | 1 | 100 | 100
H1000/1 | Incandescent | Halogen Incandescent | H1000 | Halogen Incandescent, (1) 1000W lamp |  |  | 1 | 1000 | 1000
H1200/1 | Incandescent | Halogen Incandescent | H1200 | Halogen Incandescent, (1) 1200W lamp |  |  | 1 | 1200 | 1200
H150/1 | Incandescent | Halogen Incandescent | H150 | Halogen Incandescent, (1) 150W lamp |  |  | 1 | 150 | 150
H1500/1 | Incandescent | Halogen Incandescent | H1500 | Halogen Incandescent, (1) 1500W lamp |  |  | 1 | 1500 | 1500
H200/1 | Incandescent | Halogen Incandescent | H200 | Halogen Incandescent, (1) 200W lamp |  |  | 1 | 200 | 200
H250/1 | Incandescent | Halogen Incandescent | H250 | Halogen Incandescent, (1) 250W lamp |  |  | 1 | 250 | 250
H300/1 | Incandescent | Halogen Incandescent | H300 | Halogen Incandescent, (1) 300W lamp |  |  | 1 | 300 | 300
H35/1 | Incandescent | Halogen Incandescent | H35 | Halogen Incandescent, (1) 35W lamp |  |  | 1 | 35 | 35
H350/1 | Incandescent | Halogen Incandescent | H350 | Halogen Incandescent, (1) 350W lamp |  |  | 1 | 350 | 350
H40/1 | Incandescent | Halogen Incandescent | H40 | Halogen Incandescent, (1) 40W lamp |  |  | 1 | 40 | 40
H400/1 | Incandescent | Halogen Incandescent | H400 | Halogen Incandescent, (1) 400W lamp |  |  | 1 | 400 | 400
H42/1 | Incandescent | Halogen Incandescent | H42 | Halogen Incandescent, (1) 42W lamp |  |  | 1 | 42 | 42
H425/1 | Incandescent | Halogen Incandescent | H425 | Halogen Incandescent, (1) 425W lamp |  |  | 1 | 425 | 425
H45/1 | Incandescent | Halogen Incandescent | H45 | Halogen Incandescent, (1) 45W lamp |  |  | 1 | 45 | 45
H50/1 | Incandescent | Halogen Incandescent | H50 | Halogen Incandescent, (1) 50W lamp |  |  | 1 | 50 | 50
H500/1 | Incandescent | Halogen Incandescent | H500 | Halogen Incandescent, (1) 500W lamp |  |  | 1 | 500 | 500
H52/1 | Incandescent | Halogen Incandescent | H52 | Halogen Incandescent, (1) 52W lamp |  |  | 1 | 52 | 52
H55/1 | Incandescent | Halogen Incandescent | H55 | Halogen Incandescent, (1) 55W lamp |  |  | 1 | 55 | 55
H60/1 | Incandescent | Halogen Incandescent | H60 | Halogen Incandescent, (1) 60W lamp |  |  | 1 | 60 | 60
H72/1 | Incandescent | Halogen Incandescent | H72 | Halogen Incandescent, (1) 72W lamp |  |  | 1 | 72 | 72
H75/1 | Incandescent | Halogen Incandescent | H75 | Halogen Incandescent, (1) 75W lamp |  |  | 1 | 75 | 75
H750/1 | Incandescent | Halogen Incandescent | H750 | Halogen Incandescent, (1) 750W lamp |  |  | 1 | 750 | 750
H90/1 | Incandescent | Halogen Incandescent | H90 | Halogen Incandescent, (1) 90W lamp |  |  | 1 | 90 | 90
H900/1 | Incandescent | Halogen Incandescent | H900 | Halogen Incandescent, (1) 900W lamp |  |  | 1 | 900 | 900
HLV20/1 | Incandescent | Halogen Incandescent | H20/LV | Halogen Low Voltage Incandescent, (1) 20W lamp |  |  | 1 | 20 | 30
HLV25/1 | Incandescent | Halogen Incandescent | H25/LV | Halogen Low Voltage Incandescent, (1) 25W lamp |  |  | 1 | 25 | 35
HLV35/1 | Incandescent | Halogen Incandescent | H35/LV | Halogen Low Voltage Incandescent, (1) 35W lamp |  |  | 1 | 35 | 45
HLV42/1 | Incandescent | Halogen Incandescent | H42/LV | Halogen Low Voltage Incandescent, (1) 42W lamp |  |  | 1 | 42 | 52
HLV50/1 | Incandescent | Halogen Incandescent | H50/LV | Halogen Low Voltage Incandescent, (1) 50W lamp |  |  | 1 | 50 | 60
HLV65/1 | Incandescent | Halogen Incandescent | H65/LV | Halogen Low Voltage Incandescent, (1) 65W lamp |  |  | 1 | 65 | 75
HLV75/1 | Incandescent | Halogen Incandescent | H75/LV | Halogen Low Voltage Incandescent, (1) 75W lamp |  |  | 1 | 75 | 85
H150/2 | Incandescent | Halogen Incandescent | H150 | Halogen Incandescent, (2) 150W lamp |  |  | 2 | 150 | 300
H45/2 | Incandescent | Halogen Incandescent | H45 | Halogen Incandescent, (2) 45W lamp |  |  | 2 | 45 | 90
H50/2 | Incandescent | Halogen Incandescent | H50 | Halogen Incandescent, (2) 50W lamp |  |  | 2 | 50 | 100
H55/2 | Incandescent | Halogen Incandescent | H55 | Halogen Incandescent, (2) 55W lamp |  |  | 2 | 55 | 110
H75/2 | Incandescent | Halogen Incandescent | H75 | Halogen Incandescent, (2) 75W lamp |  |  | 2 | 75 | 150
H90/2 | Incandescent | Halogen Incandescent | H90 | Halogen Incandescent, (2) 90W lamp |  |  | 2 | 90 | 180
QL55/1 | Induction Fluorescent | Induction Fluorescent | QL55 | QL Induction, (1) 55W lamp | Generator |  | 1 | 55 | 55
QL85/1 | Induction Fluorescent | Induction Fluorescent | QL85 | QL Induction, (1) 85W lamp | Generator |  | 1 | 85 | 85
QL165/1 | Induction Fluorescent | Induction Fluorescent | QL165 | QL Induction, (1) 165W lamp | Generator |  | 1 | 165 | 165
MH100/1 | High Intensity Discharge | Metal Halide | MH100 | Metal Halide, (1) 100W lamp | CWA |  | 1 | 100 | 128
MH1000/1 | High Intensity Discharge | Metal Halide | MH1000 | Metal Halide, (1) 1000W lamp | CWA |  | 1 | 1000 | 1080
MH150/1 | High Intensity Discharge | Metal Halide | MH150 | Metal Halide, (1) 150W lamp | CWA |  | 1 | 150 | 190
MH1500/1 | High Intensity Discharge | Metal Halide | MH1500 | Metal Halide, (1) 1500W lamp | CWA |  | 1 | 1500 | 1610
MH175/1 | High Intensity Discharge | Metal Halide | MH175 | Metal Halide, (1) 175W lamp | CWA |  | 1 | 175 | 215
MH1800/1 | High Intensity Discharge | Metal Halide | MH1800 | Metal Halide, (1) 1800W lamp | CWA |  | 1 | 1800 | 1875
MH200/1 | High Intensity Discharge | Metal Halide | MH200 | Metal Halide, (1) 200W lamp | CWA |  | 1 | 200 | 232
MH250/1 | High Intensity Discharge | Metal Halide | MH250 | Metal Halide, (1) 250W lamp | CWA |  | 1 | 250 | 295
MH32/1 | High Intensity Discharge | Metal Halide | MH32 | Metal Halide, (1) 32W lamp | CWA |  | 1 | 32 | 43
MH300/1 | High Intensity Discharge | Metal Halide | MH300 | Metal Halide, (1) 300W lamp | CWA |  | 1 | 300 | 342
MH320/1 | High Intensity Discharge | Metal Halide | MH320 | Metal Halide, (1) 320W lamp | CWA |  | 1 | 320 | 365
MH350/1 | High Intensity Discharge | Metal Halide | MH350 | Metal Halide, (1) 350W lamp | CWA |  | 1 | 350 | 400
MH360/1 | High Intensity Discharge | Metal Halide | MH360 | Metal Halide, (1) 360W lamp | CWA |  | 1 | 360 | 430
MH400/1 | High Intensity Discharge | Metal Halide | MH400 | Metal Halide, (1) 400W lamp | CWA |  | 1 | 400 | 458
MH450/1 | High Intensity Discharge | Metal Halide | MH450 | Metal Halide, (1) 450W lamp | CWA |  | 1 | 450 | 508
MH35/1 | High Intensity Discharge | Metal Halide | MH35 | Metal Halide, (1) 35W lamp | CWA |  | 1 | 35 | 44
MH50/1 | High Intensity Discharge | Metal Halide | MH50 | Metal Halide, (1) 50W lamp | CWA |  | 1 | 50 | 72
MH70/1 | High Intensity Discharge | Metal Halide | MH70 | Metal Halide, (1) 70W lamp | CWA |  | 1 | 70 | 95
MH750/1 | High Intensity Discharge | Metal Halide | MH750 | Metal Halide, (1) 750W lamp | CWA |  | 1 | 750 | 850
MH400/2 | High Intensity Discharge | Metal Halide | MH400 | Metal Halide, (2) 400W lamp | CWA |  | 2 | 400 | 916
MHPS/LR/100/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Linear Reactor Ballast | LR |  | 1 | 100 | 118
MHPS/LR/150/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Linear Reactor Ballast | LR |  | 1 | 150 | 170
MHPS/LR/175/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Linear Reactor Ballast | LR |  | 1 | 175 | 194
MHPS/LR/200/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Linear Reactor Ballast | LR |  | 1 | 200 | 219
MHPS/LR/250/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Linear Reactor Ballast | LR |  | 1 | 250 | 275
MHPS/LR/300/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Linear Reactor Ballast | LR |  | 1 | 300 | 324
MHPS/LR/320/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Linear Reactor Ballast | LR |  | 1 | 320 | 349
MHPS/LR/350/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Linear Reactor Ballast | LR |  | 1 | 350 | 380
MHPS/LR/400/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Linear Reactor Ballast | LR |  | 1 | 400 | 435
MHPS/LR/450/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Linear Reactor Ballast | LR |  | 1 | 450 | 485
MHPS/LR/750/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Linear Reactor Ballast | LR |  | 1 | 750 | 805
MHPS/SCWA/100/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 100 | 128
MHPS/SCWA/1000/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS1000 | Metal Halide Pulse Start, (1) 1000W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 1000 | 1080
MHPS/SCWA/150/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 150 | 190
MHPS/SCWA/175/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 175 | 208
MHPS/SCWA/200/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 200 | 232
MHPS/SCWA/250/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 250 | 288
MHPS/SCWA/300/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 300 | 342
MHPS/SCWA/320/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 320 | 368
MHPS/SCWA/350/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 350 | 400
MHPS/SCWA/400/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 400 | 450
MHPS/SCWA/450/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 450 | 506
MHPS/SCWA/750/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA |  | 1 | 750 | 815
HPS100/1 | High Intensity Discharge | High Pressure Sodium | HPS100 | High Pressure Sodium, (1) 100W lamp | CWA |  | 1 | 100 | 138
HPS1000/1 | High Intensity Discharge | High Pressure Sodium | HPS1000 | High Pressure Sodium, (1) 1000W lamp | CWA |  | 1 | 1000 | 1100
HPS150/1 | High Intensity Discharge | High Pressure Sodium | HPS150 | High Pressure Sodium, (1) 150W lamp | CWA |  | 1 | 150 | 188
HPS200/1 | High Intensity Discharge | High Pressure Sodium | HPS200 | High Pressure Sodium, (1) 200W lamp | CWA |  | 1 | 200 | 250
HPS225/1 | High Intensity Discharge | High Pressure Sodium | HPS225 | High Pressure Sodium, (1) 225W lamp | CWA |  | 1 | 225 | 275
HPS250/1 | High Intensity Discharge | High Pressure Sodium | HPS250 | High Pressure Sodium, (1) 250W lamp | CWA |  | 1 | 250 | 295
HPS310/1 | High Intensity Discharge | High Pressure Sodium | HPS310 | High Pressure Sodium, (1) 310W lamp | CWA |  | 1 | 310 | 365
HPS35/1 | High Intensity Discharge | High Pressure Sodium | HPS35 | High Pressure Sodium, (1) 35W lamp | CWA |  | 1 | 35 | 46
HPS360/1 | High Intensity Discharge | High Pressure Sodium | HPS360 | High Pressure Sodium, (1) 360W lamp | CWA |  | 1 | 360 | 414
HPS400/1 | High Intensity Discharge | High Pressure Sodium | HPS400 | High Pressure Sodium, (1) 400W lamp | CWA |  | 1 | 400 | 465
HPS50/1 | High Intensity Discharge | High Pressure Sodium | HPS50 | High Pressure Sodium, (1) 50W lamp | CWA |  | 1 | 50 | 66
HPS600/1 | High Intensity Discharge | High Pressure Sodium | HPS600 | High Pressure Sodium, (1) 600W lamp | CWA |  | 1 | 600 | 675
HPS70/1 | High Intensity Discharge | High Pressure Sodium | HPS70 | High Pressure Sodium, (1) 70W lamp | CWA |  | 1 | 70 | 95
HPS750/1 | High Intensity Discharge | High Pressure Sodium | HPS750 | High Pressure Sodium, (1) 750W lamp | CWA |  | 1 | 750 | 835
MV100/1 | High Intensity Discharge | Mercury Vapor | MV100 | Mercury Vapor, (1) 100W lamp | CWA |  | 1 | 100 | 125
MV1000/1 | High Intensity Discharge | Mercury Vapor | MV1000 | Mercury Vapor, (1) 1000W lamp | CWA |  | 1 | 1000 | 1075
MV175/1 | High Intensity Discharge | Mercury Vapor | MV175 | Mercury Vapor, (1) 175W lamp | CWA |  | 1 | 175 | 205
MV250/1 | High Intensity Discharge | Mercury Vapor | MV250 | Mercury Vapor, (1) 250W lamp | CWA |  | 1 | 250 | 290
MV40/1 | High Intensity Discharge | Mercury Vapor | MV40 | Mercury Vapor, (1) 40W lamp | CWA |  | 1 | 40 | 50
MV400/1 | High Intensity Discharge | Mercury Vapor | MV400 | Mercury Vapor, (1) 400W lamp | CWA |  | 1 | 400 | 455
MV50/1 | High Intensity Discharge | Mercury Vapor | MV50 | Mercury Vapor, (1) 50W lamp | CWA |  | 1 | 50 | 74
MV700/1 | High Intensity Discharge | Mercury Vapor | MV700 | Mercury Vapor, (1) 700W lamp | CWA |  | 1 | 700 | 780
MV75/1 | High Intensity Discharge | Mercury Vapor | MV75 | Mercury Vapor, (1) 75W lamp | CWA |  | 1 | 75 | 93
MV400/2 | High Intensity Discharge | Mercury Vapor | MV400 | Mercury Vapor, (2) 400W lamp | CWA |  | 2 | 400 | 910
Cut Sheet 1 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 2 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 3 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 4 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 5 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 6 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 7 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 8 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 9 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 10 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 11 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 12 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 13 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 14 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 15 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 16 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 17 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 18 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 19 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 20 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 21 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 22 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 23 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 24 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 25 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 26 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 27 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 28 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 29 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 30 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 31 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 32 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 33 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 34 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 35 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 36 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 37 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 38 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 39 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 40 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 41 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 42 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 43 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 44 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 45 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 46 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 47 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 48 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 49 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
Cut Sheet 50 | Custom, From Cut Sheet | Custom, From Cut Sheet | N/A | Edit | N/A |  | N/A | N/A | Edit
F26ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 24" 6-Lamp T12 EPACT/EISA Compliant T8 | N/A | 24 | 6 | 17 | 87
F36ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 36" 6-Lamp T12 EPACT/EISA Compliant T8 | N/A | 36 | 6 | 25 | 128
F61ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 1-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 1 | 65 | 55
F62ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 2-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 2 | 65 | 111
F63ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 3-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 3 | 65 | 166
F64ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 4-Lamp T12 EPACT/EISA Compliant T8 | N/A | 72 | 4 | 65 | 221
F83LHL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 96" 3-Lamp T12HO EPACT/EISA Compliant T8 | N/A | 96 | 3 | 86 | 253
F86LHL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 96" 6-Lamp T12HO EPACT/EISA Compliant T8 | N/A | 96 | 6 | 86 | 506
GSL33/1 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 33W lamp | N/A |  | 1 | 33 | 33
GSL28/1 | GSL | GFL Screw-In | GSL28 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 28W lamp | N/A |  | 1 | 28 | 28
GSL40/1 | GSL | GFL Screw-In | GSL40 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 40W lamp | N/A |  | 1 | 40 | 40
GSL44/1 | GSL | GFL Screw-In | GSL44 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 44W lamp | N/A |  | 1 | 44 | 44
GSL48/1 | GSL | GFL Screw-In | GSL48 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 48W lamp | N/A |  | 1 | 48 | 48
GSL58/1 | GSL | GFL Screw-In | GSL58 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 58W lamp | N/A |  | 1 | 58 | 58
GSL66/1 | GSL | GFL Screw-In | GSL66 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 66W lamp | N/A |  | 1 | 66 | 66
GSL8/1 | GSL | GFL Screw-In | GSL8 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 8W lamp | N/A |  | 1 | 8 | 8
GSL10/1 | GSL | GFL Screw-In | GSL10 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 10W lamp | N/A |  | 1 | 10 | 10
GSL11/1 | GSL | GFL Screw-In | GSL11 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 11W lamp | N/A |  | 1 | 11 | 11
GSL13/1 | GSL | GFL Screw-In | GSL13 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 13W lamp | N/A |  | 1 | 13 | 13
GSL14/1 | GSL | GFL Screw-In | GSL14 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 14W lamp | N/A |  | 1 | 14 | 14
GSL17/1 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 17W lamp | N/A |  | 1 | 17 | 17
GSL18/1 | GSL | GFL Screw-In | GSL18 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 18W lamp | N/A |  | 1 | 18 | 18
GSL19/1 | GSL | GFL Screw-In | GSL19 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 19W lamp | N/A |  | 1 | 19 | 19
GSL20/1 | GSL | GFL Screw-In | GSL20 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 20W lamp | N/A |  | 1 | 20 | 20
GSL23/1 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 23W lamp | N/A |  | 1 | 23 | 23
GSL25/1 | GSL | GFL Screw-In | GSL25 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 25W lamp | N/A |  | 1 | 25 | 25
GSL26/1 | GSL | GFL Screw-In | GSL26 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 26W lamp | N/A |  | 1 | 26 | 26
GSL29/1 | GSL | GFL Screw-In | GSL29 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 29W lamp | N/A |  | 1 | 29 | 29
GSL30/1 | GSL | GFL Screw-In | GSL30 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 30W lamp | N/A |  | 1 | 30 | 30
GSL33/2 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 33W lamp | N/A |  | 2 | 33 | 66
GSL40/2 | GSL | GFL Screw-In | GSL40 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 40W lamp | N/A |  | 2 | 40 | 80
GSL48/2 | GSL | GFL Screw-In | GSL48 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 48W lamp | N/A |  | 2 | 48 | 96
GSL58/2 | GSL | GFL Screw-In | GSL58 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 58W lamp | N/A |  | 2 | 58 | 116
GSL8/2 | GSL | GFL Screw-In | GSL8 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 8W lamp | N/A |  | 2 | 8 | 16
GSL10/2 | GSL | GFL Screw-In | GSL10 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 10W lamp | N/A |  | 2 | 10 | 20
GSL13/2 | GSL | GFL Screw-In | GSL13 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 13W lamp | N/A |  | 2 | 13 | 26
GSL14/2 | GSL | GFL Screw-In | GSL14 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 14W lamp | N/A |  | 2 | 14 | 28
GSL17/2 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 17W lamp | N/A |  | 2 | 17 | 34
GSL18/2 | GSL | GFL Screw-In | GSL18 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 18W lamp | N/A |  | 2 | 18 | 36
GSL19/2 | GSL | GFL Screw-In | GSL19 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 19W lamp | N/A |  | 2 | 19 | 38
GSL23/2 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 23W lamp | N/A |  | 2 | 23 | 46
GSL28/2 | GSL | GFL Screw-In | GSL28 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 28W lamp | N/A |  | 2 | 28 | 56
GSL30/2 | GSL | GFL Screw-In | GSL30 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 30W lamp | N/A |  | 2 | 30 | 60
GSL33/3 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 33W lamp | N/A |  | 3 | 33 | 99
GSL17/3 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 17W lamp | N/A |  | 3 | 17 | 51
GSL19/3 | GSL | GFL Screw-In | GSL19 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 19W lamp | N/A |  | 3 | 19 | 57
GSL23/3 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 23W lamp | N/A |  | 3 | 23 | 69
GSL28/3 | GSL | GFL Screw-In | GSL28 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (3) 28W lamp | N/A |  | 3 | 28 | 84
GSL33/4 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (4) 33W lamp | N/A |  | 4 | 33 | 132
GSL17/4 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (4) 17W lamp | N/A |  | 4 | 17 | 68
GSL23/4 | GSL | GFL Screw-In | GSL23 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (4) 23W lamp | N/A |  | 4 | 23 | 92
GSL33/5 | GSL | GFL Screw-In | GSL33 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (5) 33W lamp | N/A |  | 5 | 33 | 165
GSL17/5 | GSL | GFL Screw-In | GSL17 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (5) 17W lamp | N/A |  | 5 | 17 | 85
GSL46/1 | GSL | GFL Screw-In | GSL46 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 46W lamp | N/A |  | 1 | 46 | 46
GSL69/1 | GSL | GFL Screw-In | GSL69 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 69W lamp | N/A |  | 1 | 69 | 69
GSL12/1 | GSL | GFL Screw-In | GSL12 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 12W lamp | N/A |  | 1 | 12 | 12
GSL24/1 | GSL | GFL Screw-In | GSL24 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 24W lamp | N/A |  | 1 | 24 | 24
GSL34/1 | GSL | GFL Screw-In | GSL34 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 34W lamp | N/A |  | 1 | 34 | 34
GSL41/1 | GSL | GFL Screw-In | GSL41 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 41W lamp | N/A |  | 1 | 41 | 41
GSL9/1 | GSL | GFL Screw-In | GSL9 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (1) 9W lamp | N/A |  | 1 | 9 | 9
GSL69/2 | GSL | GFL Screw-In | GSL69 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 69W lamp | N/A |  | 2 | 69 | 138
GSL24/2 | GSL | GFL Screw-In | GSL24 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 24W lamp | N/A |  | 2 | 24 | 48
GSL34/2 | GSL | GFL Screw-In | GSL34 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 34W lamp | N/A |  | 2 | 34 | 68
GSL41/2 | GSL | GFL Screw-In | GSL41 | Baseline Code for Generic EISA Compliant General Service Lamp, Screw-in, (2) 41W lamp | N/A |  | 2 | 41 | 82

## Summary
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
SUMMARY
Project / Site Information
| Applicant Name: |  |  |  | Construction Type: |  |  | . | .
| Customer Contact: |  |  |  | Building Type: |  |  | . | .
| Installation Address: |  |  |  | Facility Size:
Total Savings
|  | Change in Connected Load | Summer Peak Demand Savings | Winter Peak Demand Savings |  | Annual Energy Savings
| Lighting Only | 0 | 0 | 0 |  | 0
| Controls Only | - | 0 | 0 |  | 0
| Total | 0 | 0 | 0 |  | 0
Fixture and Sensor Summary
| Fixtures Installed: | 0 | Wattage Controlled by Newly Installed Lighting Controls:
| Lamps Installed: | 0 |  |  |  |  | 0
| Fixtures Removed: | 0
| Lamps Removed: | 0

## Lookups
2026 TRM Appendix C: Lighting Audit & Design Tool for Commercial and Industrial Projects
LOOKUPS
|  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
| HOU and CF by Facility Type | 2: General Service Lighting | IF by Refrigeration Type |  |  |  |  | SVG by Control Type |  |  | Schedule Names | LED Code Builder |  |  | Space-by-Space LPD Option Configurator Adapted from IECC 2021 Table C405.3.2(2)
| Facility Type | 2: HOU; 3: CF_s; 4: CF_w | Refrigeration Type | IFenergy | IFdemand_s | IFdemand_w |  | Control Type | Code | SVG |  | DLC Listing Type | Length | Code | Space Type | Unit | Facility for Visually Impaired | Auditorium | Automotive facility | Convention center | Courthouse | Dining: bar lounge/leisure | Dining: cafeteria/fast food | Dining: family | Dormitory | Exercise center | Exterior | Exterior, Photocell-Controlled | Fire Station | Grocery | Gymnasium | Health-care clinic | Hospital | Hotel | Library | Manufacturing - 1 Shift | Manufacturing - 2 Shift | Manufacturing - 3 Shift | Motel | Motion picture theater | Multifamily | Museum | Office | Parking garage | Penitentiary | Performing arts theater | Police station | Post Office | Religious building | Retail | School/university | Sports arena | Street Lighting | Town hall | Transportation | Warehouse | Workshop | Other | Available List
| Education | 2: 2371; 3: 0.45; 4: 0.41 | Freezer | 0.5 | 0.5 | 0.5 |  | Light Switch | S_LS | 0% |  | 24" Linear Fluorescent Tube Replacement, Type A | 2 | LTA
| Exterior | 2: 3604; 3: 0.11; 4: 0.58 | Med. Temp. Refrg. | 0.29 | 0.29 | 0.29 |  | Occupancy Sensors | O_OS | 24% |  | 24" Linear Fluorescent Tube Replacement, Type B | 2 | LTB
| Exterior, Photocell-Controlled | 2: 4306; 3: 0.11; 4: 0.58 | High Temp. Refrg. | 0.18 | 0.18 | 0.18 |  | Time Clocks | O_TC | 24% |  | 24" Linear Fluorescent Tube Replacement, Type C | 2 | LTC | Airport Concourse | [39 empty] | 0.25
| Grocery | 2: 6471; 3: 0.93; 4: 0.84 | Unconditioned | 0 | 0 | 0 |  | Energy Management System | O_EMS | 24% |  | 36" Linear Fluorescent Tube Replacement, Type A | 3 | LTA | Atrium, < 40 ft. in height | [42 empty] | 0.48 | X
| Health | 2: 2943; 3: 0.52; 4: 0.42 | [5 empty] | Photosensors | DL_PS | 28% |  | 36" Linear Fluorescent Tube Replacement, Type B | 3 | LTB | Atrium, >= 40 ft. in height | [42 empty] | 0.6 | X
| Industrial/Manufacturing - 1 Shift | 2: 2857; 3: 0.96; 4: 0.82 | [5 empty] | Time Clocks | DL_TC | 28% |  | 36" Linear Fluorescent Tube Replacement, Type C | 3 | LTC | Audience Seating Area |  |  | 0.61 | [12 empty] | 0.23 | [8 empty] | 0.27 |  |  |  |  | 0.67 | 1.16 |  |  | 0.72 |  |  | 0.33 | [5 empty] | 0.33 | X
| Industrial/Manufacturing - 2 Shift | 2: 4730; 3: 0.96; 4: 0.82 | [5 empty] | Dimmers | PT_DIM | 31% |  | 48" Linear Fluorescent Tube Replacement, Type A | 4 | LTA | Baggage/Carousel | [39 empty] | 0.39
| Industrial/Manufacturing - 3 Shift | 2: 6631; 3: 0.96; 4: 0.82 | [5 empty] | Wireless on-off switches | PT_WS | 31% |  | 48" Linear Fluorescent Tube Replacement, Type B | 4 | LTB | Bank Activity Area | [42 empty] | 0.61 | X
| Institutional/Public Service | 2: 1419; 3: 0.23; 4: 0.19 | [5 empty] | Bi-level switches | PT_BLS | 31% |  | 48" Linear Fluorescent Tube Replacement, Type C | 4 | LTC | Chapel |  | 0.7
| Lodging | 2: 3579; 3: 0.45; 4: 0.49 | IF for Comfort Conditioned Spaces by HVAC Configuration |  |  |  |  | Computer based controls | PT_CC | 31% | 0 | 96" Linear Fluorescent Tube Replacement, Type A | 8 | LTA | Class I Facility Playing Area | [36 empty] | 2.94
| Miscellaneous / Other | 2: 2830; 3: 0.58; 4: 0.39 | [5 empty] | Pre-set scene selection | PT_PSS | 31% | Space Types | 96" Linear Fluorescent Tube Replacement, Type B | 8 | LTB | Class II Facility Playing Area | [36 empty] | 2.01
| Multi-Family Common Areas | 2: 5950; 3: 0.73; 4: 0.76 | HVAC Configuration | IFenergy | IFdemand_s | IFdemand_w | IFfossil_MMBtu | Dimmable ballasts | IT_DIM | 36% |  | 96" Linear Fluorescent Tube Replacement, Type C | 8 | LTC | Class III Facility Playing Area | [36 empty] | 1.3
| Office | 2: 2294; 3: 0.48; 4: 0.35 | AC with Fossil Fuel Heat | 0.0573 | 0.1379 | 0 | -0.001 | On-off or dimmer switches for non-personal tuning | IT_DIM | 36% |  | Troffer LED Panel |  | TLP | Class IV Facility Playing Area | [36 empty] | 0.86
| Parking Garage | 2: 8678; 3: 0.98; 4: 0.99 | AC with Electric Heat | -0.07 | 0.1379 | -0.288 | 0 | Occupancy and personal tuning/daylighting and occupancy | MT | 38% |  | High-Bay Luminaires |  | HBR | Classroom | [29 empty] | 0.89 | [12 empty] | 0.71 | X
| Restaurant | 2: 4747; 3: 0.77; 4: 0.65 | Fossil Fuel Heat Only | 0 | 0 | 0 | -0.001 | Network Lighting Controls | NLC | 49% |  | Outdoor Pole/Arm-Mounted Luminaires |  | OP/A | Computer Room/Data Center | [42 empty] | 0.94 | X
| Retail | 2: 2915; 3: 0.66; 4: 0.41 | Electric Heat Only | -0.1273 | 0 | -0.288 | 0 | <Name your custom Control type> | C_1 | 0% |  | Outdoor Wall-Mounted Luminaires |  | OW | Conference/Meeting/Multipurpose Room | [42 empty] | 0.97 | X
| Street Lighting | 3: 0; 4: 0.5 | Unknown (Market Average) | 0.0256 | 0.0813 | -0.0185 | -0.0008 | <Name your custom Control type> | C_2 | 0% |  | Refrigerated Display Case Luminaires |  | RDL | Convention Center/Exhibit Space |  |  |  |  | 0.61
| Warehouse | 2: 2545; 3: 0.48; 4: 0.37 | [5 empty] | <Name your custom Control type> | C_3 | 0% |  | Street Lamp Luminaires |  | ST | Copy/Print Room | [42 empty] | 0.31 | X
| TRM Interior | 2: #N/A; 3: #N/A; 4: #N/A | [5 empty] | <Name your custom Control type> | C_4 | 0% |  | Custom |  | C | Corridor |  | 0.71 | [15 empty] | 0.71 | [24 empty] | 0.41 | X
| TRM Exterior | 2: #N/A; 3: #N/A; 4: #N/A | [5 empty] | <Name your custom Control type> | C_5 | 0% |  |  |  |  | Courtroom | [42 empty] | 1.2 | X
| TRM Refrigeration | 2: 6205; 3: 0.92; 4: 0.92 | [5 empty] | Custom control types and corresponding SVG assumptions may be substituted when EDC data gathering (metering) produces more accurate/reliable SVG estimates. | [6 empty] | Detailed Manufacturing Area | [20 empty] | 0.8 | 0.8 | 0.8
| TRM Exit | 2: 8760; 3: 1; 4: 1 | [12 empty] | Dining Area |  | 1.27 |  |  |  |  | 0.86 | 0.4 | 0.6 | [20 empty] | 0.42 | [12 empty] | 0.43 | X
| Values in cells with blue shading will not populate unless EDC is specified in cell D18 of the "General Information" tab. | [20 empty] | Dormitory/Living Quarters | [9 empty] | 0.5 | [32 empty] | 0.5 | X
[22 empty] | Dressing Room | [30 empty] | 0.41
[22 empty] | Dressing/Fitting Room | [34 empty] | 0.51
| Lighting Power Density Allowances Space-by-Space Method | 5: Lighting Power Density Allowances Building Area Method | [12 empty] | Electrical/Mechanical Room | [42 empty] | 0.43 | X
[15 empty] | New Construction SVG Accountability | [6 empty] | Elevator Lobby | [42 empty] | 0.65 | X | bar: 2 to 3; 5 to 9
| IECC 2021 Available Space Types for Selected Building Type | LPD Allowance | Unit |  | IECC 2021 Building Type |  |  | LPD | SWE Facility Type | [12 empty] | Emergency Vehicle Garage | [42 empty] | 0.52 | X
[15 empty] | Facility Type | % Req. | NC SVG |  |  |  |  | Equipment Room | [20 empty] | 0.76 | 0.76 | 0.76
| NEW CONSTRUCTION WHOLE BUILDING | 5: Automotive facility; 8: 0.75; 9: Miscellaneous / Other | [5 empty] | Education | 69% | 16.56% |  |  |  |  | Exam/Treatment Room | [16 empty] | 1.4 | 1.4
11 | Atrium, < 40 ft. in height | 5: Convention center; 8: 0.64; 9: Miscellaneous / Other | [5 empty] | Exterior | - | 0% |  |  |  |  | Extra High Bay Area, Greater than 50' Ceiling | [20 empty] | 1.42 | 1.42 | 1.42
12 | Atrium, >= 40 ft. in height | 5: Courthouse; 8: 0.79; 9: Institutional/Public Service | [5 empty] | Grocery | 20% | 4.8% |  |  |  |  | Fellowship Hall | [33 empty] | 0.54
13 | Audience Seating Area | 5: Dining: bar lounge/leisure; 8: 0.8; 9: Restaurant | [5 empty] | Health | 32% | 7.68% | 0 |  |  |  | Fire Station/Sleeping Quarters | [13 empty] | 0.23 | [28 empty] | 0.23 | X
15 | Bank Activity Area | 5: Dining: cafeteria/fast food; 8: 0.76; 9: Restaurant | [5 empty] | Industrial/Manufacturing - 1 Shift | - | 0% |  |  |  |  | Food Preparation Area | [42 empty] | 1.09 | X
21 | Classroom | 5: Dining: family; 8: 0.71; 9: Restaurant | [5 empty] | Industrial/Manufacturing - 2 Shift | - | 0% |  |  |  |  | General Exhibition Area | [26 empty] | 0.31
22 | Computer Room/Data Center | 5: Dormitory; 8: 0.53; 9: Education | [5 empty] | Industrial/Manufacturing - 3 Shift | - | 0% |  |  |  |  | Guest Room | [42 empty] | 0.41 | X
23 | Conference/Meeting/Multipurpose Room | 5: Exercise center; 8: 0.72; 9: Health | [5 empty] | Institutional/Public Service | 51% | 12.24% |  |  |  |  | Gymnasium Exercise Area | [15 empty] | 0.9
25 | Copy/Print Room | 5: Exterior; 9: Exterior | [5 empty] | Lodging | 61% | 14.64% |  |  |  |  | Gymnasium Play Area | [15 empty] | 0.85
26 | Corridor | 5: Exterior, Photocell-Controlled; 9: Exterior, Photocell-Controlled | [5 empty] | Miscellaneous / Other | 24% | 5.76% |  |  |  |  | High Bay Area, 25' to 50' Ceiling | [20 empty] | 1.24 | 1.24 | 1.24
27 | Courtroom | 5: Fire Station; 8: 0.56; 9: Institutional/Public Service | [5 empty] | Office | 62% | 14.88% |  |  |  |  | Imaging Room | [16 empty] | 0.94 | 0.94
29 | Dining Area | 5: Grocery; 8: 0.84; 9: Grocery | [5 empty] | Parking Garage | - | 0% |  |  |  |  | Laboratory | [35 empty] | 1.11 | [6 empty] | 1.33 | X
30 | Dormitory/Living Quarters | 5: Gymnasium; 8: 0.76; 9: Health | [5 empty] | Restaurant | 21% | 5.04% |  |  |  |  | Laundry/Washing Area | [42 empty] | 0.53 | X
33 | Electrical/Mechanical Room | 5: Health-care clinic; 8: 0.81; 9: Health | [5 empty] | Retail | 21% | 5.04% |  |  |  |  | Library Reading Area | [19 empty] | 0.96
34 | Elevator Lobby | 5: Hospital; 8: 0.96; 9: Health | [5 empty] | Warehouse | 60% | 14.4% |  |  |  |  | Library Stacks | [19 empty] | 1.18
35 | Emergency Vehicle Garage | 5: Hotel; 8: 0.56; 9: Lodging | [5 empty] | <Name your custom Facility type> |  | 0% |  |  |  |  | Loading dock, interior | [42 empty] | 0.88 | X
40 | Fire Station/Sleeping Quarters | 5: Library; 8: 0.83; 9: Institutional/Public Service | [5 empty] | <Name your custom Facility type> |  | 0% |  |  |  |  | Lobby |  | 1.69 | [16 empty] | 0.51 | [5 empty] | 0.23 | [5 empty] | 1.25 | [11 empty] | 0.84 | X
41 | Food Preparation Area | 5: Manufacturing - 1 Shift; 8: 0.82; 9: Industrial/Manufacturing - 1 Shift | [5 empty] | <Name your custom Facility type> |  | 0% |  |  |  |  | Locker Room | [42 empty] | 0.52 | X
43 | Guest Room | 5: Manufacturing - 2 Shift; 8: 0.82; 9: Industrial/Manufacturing - 2 Shift | [5 empty] | <Name your custom Facility type> |  | 0% |  |  |  |  | Lounge/Breakroom | [16 empty] | 0.42 | 0.42 | [24 empty] | 0.59 | X
48 | Laboratory | 5: Manufacturing - 3 Shift; 8: 0.82; 9: Industrial/Manufacturing - 3 Shift | [5 empty] | <Name your custom Facility type> |  | 0% |  |  |  |  | Low Bay Area, Less than 25' Ceiling | [20 empty] | 0.86 | 0.86 | 0.86
49 | Laundry/Washing Area | 5: Motel; 8: 0.56; 9: Lodging | [5 empty] | % Req. column dictates the percentage of the total area of each building type found to be a space type requiring occupancy sensors by code per the Commercial Light Metering Study. | [6 empty] | Mall Concourse | [34 empty] | 0.82
52 | Loading dock, interior | 5: Motion picture theater; 8: 0.44; 9: Miscellaneous / Other | [12 empty] | Medical Supply Room | [16 empty] | 0.62 | 0.62
53 | Lobby | 5: Multifamily; 8: 0.45; 9: Lodging | [12 empty] | Nursery | [16 empty] | 0.92 | 0.92
54 | Locker Room | 5: Museum; 8: 0.55; 9: Institutional/Public Service | [5 empty] | Custom facility types and corresponding SVG assumptions may be substituted when default assumptions are not reflective of code baseline conditions. | [6 empty] | Nurse's Station | [16 empty] | 1.17 | 1.17
55 | Lounge/Breakroom | 5: Office; 8: 0.64; 9: Office | [12 empty] | Office, Enclosed | [42 empty] | 0.74 | X
61 | Office, Enclosed | 5: Parking garage; 8: 0.18; 9: Parking Garage | [12 empty] | Office, Open Plan | [42 empty] | 0.61 | X
62 | Office, Open Plan | 5: Penitentiary; 8: 0.69; 9: Institutional/Public Service | [12 empty] | Operating Room | [16 empty] | 2.26 | 2.26
64 | Parking Area, Interior | 5: Performing arts theater; 8: 0.84; 9: Miscellaneous / Other | [12 empty] | Parking Area, Interior | [42 empty] | 0.15 | X
66 | Pharmacy Area | 5: Police station; 8: 0.66; 9: Institutional/Public Service | [12 empty] | Patient Room | [16 empty] | 0.68 | 0.68
71 | Restroom | 5: Post office; 8: 0.65; 9: Institutional/Public Service | [12 empty] | Pharmacy Area | [42 empty] | 1.66 | X
72 | Sales Area | 5: Religious building; 8: 0.67; 9: Institutional/Public Service | [12 empty] | Physical Therapy Room | [16 empty] | 0.91 | 0.91
73 | Seating Area, General | 5: Retail; 8: 0.84; 9: Retail | [12 empty] | Recovery Room | [16 empty] | 1.25 | 1.25
75 | Stairwell | 5: School/university; 8: 0.72; 9: Education | [12 empty] | Recreation Room |  | 1.77
78 | Storage Room | 5: Sports arena; 8: 0.76; 9: Miscellaneous / Other | [12 empty] | Restoration Room | [26 empty] | 1.1
80 | Vehicular Maintenance Area | 5: Street Lighting; 9: Street Lighting | [12 empty] | Restroom |  | 1.26 | [40 empty] | 0.63 | X
81 | Workshop | 5: Town hall; 8: 0.69; 9: Institutional/Public Service | [12 empty] | Sales Area | [42 empty] | 1.05 | X
84 | Base Site Allowance | 3: Site; 5: Transportation; 8: 0.5; 9: Miscellaneous / Other | [12 empty] | Seating Area, General | [42 empty] | 0.23 | X
85 | Uncovered Parking Areas and Drives | 3: W/ft2; 5: Warehouse; 8: 0.45; 9: Warehouse | [12 empty] | Sorting area | [32 empty] | 0.76
86 | Building Grounds: Walkways and ramps less than 10' Wide | 3: W/linear foot; 5: Workshop; 8: 0.91; 9: Industrial/Manufacturing - 1 Shift | [12 empty] | Stairwell | [42 empty] | 0.49 | X
87 | Building Grounds: Walkways and ramps 10' Wide or Greater, plaza areas, special feature areas | 3: W/ft2; 5: Values written in blue were added for functionality reasons and are not directly from IECC. | [12 empty] | Storage Area for Medium to Bulky (Palletized) Items | [40 empty] | 0.33
88 | Building Grounds: Dining areas | 3: W/ft2 | [12 empty] | Storage Area for Smaller Hand-Carried Items | [40 empty] | 0.69
89 | Building Grounds: Stairways | 3: W/ft2 | [12 empty] | Storage Room | [42 empty] | 0.38 | X
90 | Building Grounds: Pedestrian Tunnels | 3: W/ft2 | [12 empty] | Terminal Ticket Counter | [39 empty] | 0.51
91 | Building Grounds: Landscaping | 3: W/ft2 | [12 empty] | Vehicular Maintenance Area | [42 empty] | 0.6 | X
92 | Building Entrances and Exits: Pedestrians and vehicular entrances and exits | 3: Linear Foot of Opening | [12 empty] | Workshop | [42 empty] | 1.26 | X
93 | Building Entrances and Exits: Entry Canopies | 3: W/ft2 | [12 empty] | Worship/Pulpit/Choir Area | [33 empty] | 0.85
94 | Building Entrances and Exits: Loading docks | 3: W/ft2 | [12 empty] | Exterior Space Types | Unit | [42 empty] | Available List
95 | Sales Canopies, free-standing and attached | 3: W/ft2 | [12 empty] | Base Site Allowance | Site | 350 | 400 | 500 | 900 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
96 | Outdoor Sales, Open Areas (including vehicles sales lots) | 3: W/ft2 | [12 empty] | Uncovered Parking Areas and Drives | W/ft2 | 0.03 | 0.04 | 0.06 | 0.08 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
97 | Outdoor Sales, Street Frontage for vehicle sales lots in addition to "open area" allowance | 3: W/linear foot | [12 empty] | Building Grounds: Walkways and ramps less than 10' Wide | W/linear foot | 0.5 | 0.5 | 0.6 | 0.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
98 | Building Facades | 3: W/ft2 S.F. of gross above-grade wall area | [12 empty] | Building Grounds: Walkways and ramps 10' Wide or Greater, plaza areas, special feature areas | W/ft2 | 0.1 | 0.1 | 0.11 | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
99 | ATM and night depositories, first location | 3: W/Location | [12 empty] | Building Grounds: Dining areas | W/ft2 | 0.65 | 0.65 | 0.75 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
100 | ATM and night depositories, additional locations | 3: W/Location | [12 empty] | Building Grounds: Stairways | W/ft2 | 0.6 | 0.7 | 0.7 | 0.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
101 | Uncovered entrances and gatehouse inspection stations at guarded facilities | 3: W/ft2 of area | [12 empty] | Building Grounds: Pedestrian Tunnels | W/ft2 | 0.12 | 0.12 | 0.14 | 0.21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
102 | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency services vehicles | 3: W/ft2 of area | [12 empty] | Building Grounds: Landscaping | W/ft2 | 0.03 | 0.04 | 0.04 | 0.04 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
103 | Drive-Up Windows & Doors | 3: W/Drive Through | [12 empty] | Building Entrances and Exits: Pedestrians and vehicular entrances and exits | Linear Foot of Opening | 14 | 14 | 21 | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
104 | Parking near 24-Hour retail entrances | 3: W/Main Entry | [12 empty] | Building Entrances and Exits: Entry Canopies | W/ft2 | 0.2 | 0.25 | 0.4 | 0.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Building Entrances and Exits: Loading docks | W/ft2 | 0.35 | 0.35 | 0.35 | 0.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Sales Canopies, free-standing and attached | W/ft2 | 0.4 | 0.4 | 0.6 | 0.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Outdoor Sales, Open Areas (including vehicles sales lots) | W/ft2 | 0.2 | 0.2 | 0.35 | 0.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Outdoor Sales, Street Frontage for vehicle sales lots in addition to "open area" allowance | W/linear foot | 0 | 7 | 7 | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Building Facades | W/ft2 S.F. of gross above-grade wall area | 0 | 0.075 | 0.113 | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | ATM and night depositories, first location | W/Location | 135 | 135 | 135 | 135 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | ATM and night depositories, additional locations | W/Location | 45 | 45 | 45 | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Uncovered entrances and gatehouse inspection stations at guarded facilities | W/ft2 of area | 0.5 | 0.5 | 0.5 | 0.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency services vehicles | W/ft2 of area | 0.35 | 0.35 | 0.35 | 0.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Drive-Up Windows & Doors | W/Drive Through | 200 | 200 | 200 | 200 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
[22 empty] | Parking near 24-Hour retail entrances | W/Main Entry | 400 | 400 | 400 | 400 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | X
| 57 | [20 empty] | Individual Lighting Power Allowances for Building Exteriors Adapted from IECC 2021 Tables C405.5.2(2) and C405.5.2(3)
[22 empty] | Space Type | Unit | Zone 1 | Zone 2 | Zone 3 | Zone 4
[22 empty] | Base Site Allowance | Site | 350 | 400 | 500 | 900
[22 empty] | Uncovered Parking Areas and Drives | W/ft2 | 0.03 | 0.04 | 0.06 | 0.08
[22 empty] | Building Grounds: Walkways and ramps less than 10' Wide | W/linear foot | 0.5 | 0.5 | 0.6 | 0.7
[22 empty] | Building Grounds: Walkways and ramps 10' Wide or Greater, plaza areas, special feature areas | W/ft2 | 0.1 | 0.1 | 0.11 | 0.14
[22 empty] | Building Grounds: Dining areas | W/ft2 | 0.65 | 0.65 | 0.75 | 0.95
[22 empty] | Building Grounds: Stairways | W/ft2 | 0.6 | 0.7 | 0.7 | 0.7
[22 empty] | Building Grounds: Pedestrian Tunnels | W/ft2 | 0.12 | 0.12 | 0.14 | 0.21
[22 empty] | Building Grounds: Landscaping | W/ft2 | 0.03 | 0.04 | 0.04 | 0.04
[22 empty] | Building Entrances and Exits: Pedestrians and vehicular entrances and exits | Linear Foot of Opening | 14 | 14 | 21 | 21
[22 empty] | Building Entrances and Exits: Entry Canopies | W/ft2 | 0.2 | 0.25 | 0.4 | 0.4
[22 empty] | Building Entrances and Exits: Loading docks | W/ft2 | 0.35 | 0.35 | 0.35 | 0.35
[22 empty] | Sales Canopies, free-standing and attached | W/ft2 | 0.4 | 0.4 | 0.6 | 0.7
[22 empty] | Outdoor Sales, Open Areas (including vehicles sales lots) | W/ft2 | 0.2 | 0.2 | 0.35 | 0.5
[22 empty] | Outdoor Sales, Street Frontage for vehicle sales lots in addition to "open area" allowance | W/linear foot | 0 | 7 | 7 | 21
[22 empty] | Building Facades | W/ft2 S.F. of gross above-grade wall area | 0 | 0.075 | 0.113 | 0.15
[22 empty] | ATM and night depositories, first location | W/Location | 135 | 135 | 135 | 135
[22 empty] | ATM and night depositories, additional locations | W/Location | 45 | 45 | 45 | 45
[22 empty] | Uncovered entrances and gatehouse inspection stations at guarded facilities | W/ft2 of area | 0.5 | 0.5 | 0.5 | 0.5
[22 empty] | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency services vehicles | W/ft2 of area | 0.35 | 0.35 | 0.35 | 0.35
[22 empty] | Drive-Up Windows & Doors | W/Drive Through | 200 | 200 | 200 | 200
[22 empty] | Parking near 24-Hour retail entrances | W/Main Entry | 400 | 400 | 400 | 400
Note on AJ13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IECC 2021 excludes this previously included category
Note on BO13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed. Building type not included for space type in IECC 2021
Note on AZ26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Excluded from “Corridor” in IECC 2021
Note on BA26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Excluded from “Corridor” in IECC 2021
Note on BB26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Excluded from “Corridor” in IECC 2021
Note on BO48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Referred to as “in or as a classroom” in IECC 2021