## Manual
Pennsylvania Act 129 Motor & VFD Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Motor & VFD Audit and Design Tool is two-fold:
1. To document the pre- and post-installation cases.
2. To facilitate the calculation of energy savings and demand reduction for motor and VFD installations.
II. Organization
The Motor & VFD Audit and Design Tool is organized into 6 sheets.
(1) Manual
The "Manual" sheet contains the instruction manual for using the Motor & VFD Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) General Information
The "General Information" sheet should be populated with basic information about the project, like project and facility name. Fields for Utility, Facility Type, and Weather Location are necessary to properly pull in default values from the TRM.
(4) 3.3.1 Premium Efficiency Motors
The "3.3.1 Premium Efficiency Motors" sheet collects all relevant information to calculate energy savings and peak demand reduction for motor replacements. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. Note that the requirements of Section 3.3.1 (Premium Efficiency Motors) in the 2026 TRM restrict the protocol to only motor replacements without VFDs. This form must be used to calculate savings for motor replacement measures only (i.e. replacement of old motors with new energy efficient motors of the same rated horsepower).
The energy efficiency motor and configuration details should be entered in the "Post-Retrofit Details" section (columns E-N). Baseline motor efficiency will be automatically populated using tables as defined in the 2026 TRM. The energy and peak demand savings resulting from the motor replacement alone will be automatically calculated in cells AD6 and AC6 respectively. To calculate savings resulting from VFD measures, refer to the notes described below.
(5) 3.3.2 VFD Improvements
The "3.3.2 VFD Improvements" sheet collects all relevant information to calculate energy savings and peak demand reduction for VFDs. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. This form must be used to calculate savings for VFD measures only, not the combination of new motors and VFDs.
The motor and configuration details should be entered in the "Post-Retrofit Details" section (Columns E-N) for a motor with VFD. A custom motor load profile can be selected if the appropriate fields are populated on the 'VFD Custom Load Profile' tab. Select the baseline control configuration from the pull down menu in Column O. The energy and peak demand savings resulting from installation of a VFD will be automatically calculated in cells BF6 and BE6 respectively. Note that custom protocols must be followed if the existing motor already has a VFD installed or if the VFD Baseline is not listed in the options.
(6) VFD Custom Load Profile
The "VFD Custom Load Profile" sheet should be used to define custom fan or pump load profiles for a VFD project. Up to 10 custom profiles can be entered.
(7) Lookups
This tab houses lookup tables used in both the motor and VFD calculation worksheets. Tables taken from the TRM include default hours of use and motor baseline efficiency.
III. User Guide
The tool contains all information regarding motors and VFDs required for the calculation of savings pursuant to the PA TRM. The use of this tool is encouraged but not required. Users of the Motor and VFD Audit and Design Tool must complete the "Motor Inventory" and/or "VFD Inventory" depending on the measures installed for the project. For VFD measures in conjunction with a motor replacement measure, the savings must be calculated separately using the "Motor Form" and "VFD Form". To find out how to calculate savings resulting from motor replacement and VFD measures separately, refer to the notes described above. The designer must select the appropriate facility type, utility, and weather file from the drop down menu. Use one line for each unique motor, i.e. motors with different operating conditions or different motor specifications. Complete all green fields to calculate the peak demand reduction and annual energy savings. Gray fields are computed automatically. Roll mouse over the field heading for additional help. Projects with facility types or motor functions not included on the drop down menu must follow custom protocols to determine appropriate run hours and coincidence factor values. Motor replacements with the following conditions should also follow custom protocols:
* Variable frequency drive (VFD) control on the existing (baseline) motor
* Two-speed motor (existing and/or new)
* Single speed motor with variable loading (not standard)
* Industrial process applications
* Applications where the building type or motor usage group is not listed in Table 3-84 through 3-96 of the 2026 TRM
* New motor has a different rated horsepower than the existing motor
* Change in annual operating hours is anticipated
IV. Disclaimer
This document does not modify any requirements of the PA TRM and is provided for convenience only. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## General Information
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
GENERAL INFORMATION
| KEY: | Input Field |  |  | Example Cell |  | Cell Creating Error in Calculations
|  | Calculated Value |  |  | Intermediate Calc.
❶ Project / Site Information
Provide basic project information below.
Applicant Name:
Facility Name:
Installation Address:
| City: |  |  | State: |  | Zip:
| Utility: | Duquesne Light | Account No.:
Contact Name & Title:
Phone:
Email:
| Facility Type: | Grocery
| Weather Location: | Binghamton
| Installation Date: | 2024-04-10

## 3.3.1 Premium Efficiency Motors
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
3.3.1 Premium Efficiency Motors
MOTORS Total
[29 empty] | 0 | 0 | 0
SAVINGS
|  |  |  | POST-RETROFIT DETAILS | [9 empty] | BASELINE DETAILS |  |  | Analysis | [11 empty] | MOTORS
Line Item | Program Year | Unique Motor I.D.(s) | Motor Function | Manufacturer | Model Number | Motor Horsepower | NEMA Design Type | Number of Poles | Enclosure Type | Motor Efficiency | Number of Identical Units | Default Load Factor (LF) | Custom Load Factor (LF) | Default Annual Run Hours | Custom Annual Run Hours | Baseline Nominal Efficiency | Analysis Hours | Analysis LF | Energy to Demand Factor, Summer | Energy to Demand Factor, Winter | Base Full Load kW | Base Annual kWh | Base Peak kW, Summer | Base Peak kW, Winter | Energy Efficient Full Load kW | Energy Efficient Annual kWh | Energy Efficient Peak kW, Summer | Energy Efficient Peak kW, Winter | Energy (kWh) | Peak Demand, Summer (kW) | Peak Demand, Winter (kW) | Lamps Removed Counter | Lamps Installed Counter
Ex. | PY18 | CHWP-1 | SF | Baldor | A12345 | 10 | NEMA Design A | 4 | ODP | 96% | 2 | 0.76 |  | 6735 |  | 91.7% | 6735 | 0.76 | 0.0001853 | 0.0001143 | 12.3655 | 83281.9106 | 15.4321 | 9.5191 | 11.8117 | 79551.575 | 14.7409 | 9.0927 | 3730.3356 | 0.69123 | 0.42638
1 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
2 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
3 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
4 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
5 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
6 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
7 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
8 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
9 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
10 | [11 empty] | N/A |  | N/A |  | 0% | N/A | N/A | N/A | N/A
Note on J10: Mary-Hall: 3600 RPM 2 Pole 1800 RPM 4 Pole 1200 RPM 6 Pole 900 RPM 8 Pole
Note on N10: Mary-Hall: default value is 0.79 for pumps and 0.76 for fans
Note on O10: Mary-Hall: Use this column to overwrite the default.
Note on Q10: Mary-Hall: Enter custom operating hours to override the default

## 3.3.2 VFD Improvements
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
3.3.3 Variable Frequency Drive (VFD) Improvements
Total VFDs
[58 empty] | 0 | 0 | 0
SAVINGS
|  |  | POST-RETROFIT DETAILS | [11 empty] | BASELINE DETAILS | Load Profile | [10 empty] | Baseline Power Part Load Ratios | [10 empty] | VFD Power Part Load Ratios | [10 empty] | Analysis
Line Item | Unique Motor I.D.(s) | Motor Function | Manufacturer | Model Number | Motor Horsepower | Motor Efficiency | Default Load Factor (LF) | Custom Load Factor (LF) | Default Annual Run Hours | Custom Annual Run Hours | Load Profile | Power Part Load Ratio | Avg Flow Fraction During Summer Peak | Avg Flow Fraction During Winter Peak | Baseline Control Type | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | Analysis Hours | Analysis LF | Full Load kW | Summer Base Peak kW | Winter Base Peak kW | Base Annual kWh | Energy Efficient Summer Peak kW | Energy Efficient Winter Peak kW | Energy Efficient Annual kWh | Summer Peak Demand (kW) | Winter Peak Demand (kW) | Energy (kWh)
Ex. | SF-1 | SF | Baldor | A12345 | 10 | 90.5% | 0.76 |  | 6735 |  | HVAC fan | Fan: VFD with Duct Static Pressure Controls | 90% | 70% | Fan: Constant Volume | 0% | 0% | 1% | 5% | 16% | 22% | 25% | 19% | 9% | 3% | 0% | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [11 empty] | 6735 | 0.76 | 6.2648 | 6.2648 | 6.2648 | 42193.1006 |  |  | 0 |  |  | 42193.1006
1 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
2 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
3 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
4 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
5 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
6 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
7 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
8 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
9 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
10 | [6 empty] | N/A |  | N/A | [39 empty] | N/A | N/A
Note on I10: Mary-Hall: default value is 0.79 for pumps and 0.76 for fans
Note on J10: Mary-Hall: Use this column to overwrite the default.
Note on L10: Mary-Hall: Enter custom operating hours to override the default
Note on O10: Josh Baker: Default Values… 90%: CHWP, CTF, CW Pump, and SF 0%: HHW
Note on P10: Mary-Hall: Default Values… 0%: CHWP, CTF, and CW Pump 70%: HHW and SF

## VFD Custom Load Profile
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
VFD Custom Load Profile Input
% Capacity | Default HVAC Fan | Default HVAC Pump | Custom Load Profile 1 | Custom Load Profile 2 | Custom Load Profile 3 | Custom Load Profile 4 | Custom Load Profile 5 | Custom Load Profile 6 | Custom Load Profile 7 | Custom Load Profile 8 | Custom Load Profile 9 | Custom Load Profile 10 | MOTORS | Total
0% | 0% | 0%
10% | 0% | 0%
20% | 1% | 0%
30% | 5% | 5%
40% | 16% | 10%
50% | 22% | 20%
60% | 25% | 30%
70% | 19% | 20%
80% | 9% | 10%
90% | 3% | 5%
100% | 0% | 0%
Total | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Note on E5: Mary-Hall: Load Profile can be renamed
Note on F5: Mary-Hall: Load profile can be renamed
Note on G5: Mary-Hall: Load profile can be renamed
Note on H5: Mary-Hall: Load Profile can be renamed
Note on I5: Mary-Hall: Load Profile can be renamed
Note on J5: Mary-Hall: Load Profile can be renamed
Note on K5: Mary-Hall: Load Profile can be renamed
Note on L5: Mary-Hall: Load Profile can be renamed
Note on M5: Mary-Hall: Load Profile can be renamed
Note on N5: Mary-Hall: Load Profile can be renamed
Note on E17: Mary-Hall: Total should equal 100%.
Note on F17: Mary-Hall: Total should equal 100%.
Note on G17: Mary-Hall: Total should equal 100%.

## Lookups
Phase V TRM Appendix D: Motor & VFD Audit and Design Tool
LOOKUPS
[17 empty] | Tables 3-87 through 3-91 | [11 empty] | Table 3-92 Default ETDFs for Fan and Pump Motors in Commercial Buildings | [6 empty] | Table 3-94: Default Load Profiles for HVAC Fans and Pumps
| Table 3‑84: Baseline Efficiencies for NEMA Design A and NEMA Design B Motors | [8 empty] | Table 3‑86: Baseline Motor Nominal Full-Load Efficiencies for NEMA Design C Motors | [6 empty] | Application | Facility Type | Allentown | Binghamton | Bradford | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | Default Load Factor | Facility Type | Parameter | Supply Fan Motors | Chilled Water Pump Motors | Cooling Tower Fan Motors | Heating Hot Water Pump Motors | Condenser Water Pump Motors | Flow Fraction (%) | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
Motor Function | HP | 2 Pole (3600 RPM) |  | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) |  | HP | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) |  | SF | Education - College/University | 5798 | 6028 | 5419 | 5720 | 4955 | 5756 | 5646 | 5513 | 5818 | 0.76 | - | - | SF | CHWP | CTF | HHWP | CW Pump | HVAC Fan | 0% | 0% | 1% | 5% | 16% | 22% | 25% | 19% | 9% | 3% | 0%
CHWP |  | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open |  | Enclosed | Open | Enclosed | Open | Enclosed | Open | SF | Education - Other | 4203 | 4563 | 4174 | 4260 | 3647 | 4230 | 4167 | 4212 | 4313 |  | Education - College/University | ETDFs | 0.000163 | 0.0005511 | 0.0004543 | 7.89e-05 | 0.0005511 | HVAC Pump | 0% | 0% | 0% | 5% | 10% | 20% | 30% | 20% | 10% | 5% | 0%
CTF |  | TEFC2 | ODP2 | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | HP | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | SF | Grocery | 6437 | 6735 | 6024 | 6278 | 5659 | 6435 | 6340 | 6309 | 6612 |  | Education - College/University | ETDFw | 0.0001443 | 7.6e-06 | 1.33e-05 | 0.0002103 | 7.6e-06 | Custom Load Profile 1 | bar: 0% to 100%
CW Pump | 1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% | 75.5% | 1 | 85.5% | 85.5% | 82.5% | 82.5% | 75.5% | 75.5% | SF | Health - Hospital | 8406 | 8722 | 7749 | 8162 | 7407 | 8452 | 8268 | 8219 | 8631 |  | Education - Other | ETDFs | 0.000163 | 0.0005511 | 0.0004543 | 7.89e-05 | 0.0005511 | Custom Load Profile 2 | bar: 0% to 100%
HHWP | 1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | 1.5 | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | SF | Health - Other | 8406 | 8722 | 7749 | 8162 | 7407 | 8452 | 8268 | 8219 | 8631 |  | Education - Other | ETDFw | 0.0001443 | 7.6e-06 | 1.33e-05 | 0.0002103 | 7.6e-06 | Custom Load Profile 3 | bar: 0% to 100%
SF | 2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | 2 | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | SF | Industrial Manufacturing | 3676 | 3964 | 3609 | 3705 | 3187 | 3703 | 3652 | 3661 | 3773 |  | Grocery | ETDFs | 0.0001853 | 0 | 0 | 0 | 0 | Custom Load Profile 4 | bar: 0% to 100%
| 3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | 3 | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | SF | Institutional/Public Service | 4979 | 5201 | 4643 | 4861 | 4373 | 5004 | 4909 | 4885 | 5108 |  | Grocery | ETDFw | 0.0001143 | 0 | 0 | 0 | 0 | Custom Load Profile 5 | bar: 0% to 100%
Utility | 5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | 5 | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | SF | Lodging | 8406 | 8722 | 7749 | 8162 | 7407 | 8452 | 8268 | 8219 | 8631 |  | Health - Hospital | ETDFs | 0.0001222 | 0.0003023 | 0.0002982 | 0.0001047 | 0.0003023 | Custom Load Profile 6 | bar: 0% to 100%
Duquesne Light | 7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | 7.5 | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | SF | Office | 4026 | 4454 | 4157 | 4138 | 3456 | 3920 | 4002 | 3967 | 4078 |  | Health - Hospital | ETDFw | 0.0001036 | 1.15e-05 | 1.04e-05 | 0.000132 | 1.15e-05 | Custom Load Profile 7 | bar: 0% to 100%
Met-Ed (FirstEnergy) | 10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | 10 | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | SF | Restaurant | 6028 | 2668 | 5739 | 5930 | 5287 | 6007 | 5946 | 5925 | 6194 |  | Health - Other | ETDFs | 0.0001509 | 0.0003904 | 0.0003793 | 0.0001393 | 0.0003904 | Custom Load Profile 8 | bar: 0% to 100%
Penn Power (FirstEnergy) | 15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | 15 | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | SF | Retail | 4930 | 5166 | 4630 | 4806 | 4319 | 4913 | 4857 | 4831 | 5059 |  | Health - Other | ETDFw | 0.0001266 | 1.77e-05 | 1.18e-05 | 0.000122 | 1.77e-05 | Custom Load Profile 9 | bar: 0% to 100%
Penelec (FirstEnergy) | 20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | 20 | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | SF | Warehouse - Other | 4834 | 5167 | 4652 | 4865 | 4211 | 4987 | 4823 | 4867 | 4954 |  | Industrial Manufacturing | ETDFs | 0.000195 | 0.0006284 | 0.0006211 | 0 | 0.0006284 | Custom Load Profile 10 | bar: 0% to 100%
West Penn Power (FirstEnergy) | 25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | 25 | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | SF | Warehouse - Refrigerated | 3878 | 4024 | 3575 | 3765 | 3417 | 3899 | 3814 | 3791 | 3982 |  | Industrial Manufacturing | ETDFw | 0.0001268 | 4e-06 | 2e-07 | 0 | 4e-06
PECO | 30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | 30 | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | CHWP | Education - College/University | 5450 | 3402 | 4303 | 5061 | 4503 | 5259 | 4621 | 5321 | 4414 | 0.79 | Institutional / Public Service | ETDFs | 0.0001674 | 0 | 0 | 0 | 0
PPL | 40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | 40 | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | CHWP | Education - Other | 3701 | 1831 | 2267 | 3023 | 3030 | 4276 | 3158 | 3211 | 2933 |  | Institutional / Public Service | ETDFw | 0.0001136 | 0 | 0 | 0 | 0
| 50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | 50 | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | CHWP | Grocery | [10 empty] | Lodging | ETDFs | 0.0001845 | 0.0002853 | 0.0002514 | 8.62e-05 | 0.0002853
Facility Types | 60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | 60 | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | CHWP | Health - Hospital | 7600 | 4753 | 5792 | 7102 | 6346 | 7425 | 6600 | 7320 | 6416 |  | Lodging | ETDFw | 0.000116 | 4.65e-05 | 5.2e-06 | 0.0001165 | 4.65e-05
Education - College/University | 75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | 75 | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | CHWP | Health - Other | 5293 | 3062 | 3603 | 4804 | 4555 | 5533 | 4602 | 5157 | 4353 |  | Office | ETDFs | 0.0001769 | 0.0005857 | 0.0005877 | 0.0001947 | 0.0005857
Education - Other | 100 | 94.1% | 93.6% | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% | 100 | 95.4% | 95.4% | 95% | 95% | 93.6% | 94.1% | CHWP | Industrial Manufacturing | 2360 | 1293 | 1510 | 2013 | 1934 | 2307 | 1895 | 2166 | 1862 |  | Office | ETDFw | 0.0001345 | 5e-06 | 3.4e-06 | 0.0001874 | 5e-06
Grocery | 125 | 95% | 94.1% | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% | 125 | 95.4% | 95.4% | 95% | 95% | 94.1% | 94.1% | CHWP | Institutional/Public Service | [10 empty] | Restaurant | ETDFs | 0.0001565 | 0 | 0 | 0 | 0
Health - Hospital | 150 | 95% | 94.1% | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% | 150 | 95.8% | 95.8% | 95.8% | 95.4% | 94.1% | 94.1% | CHWP | Lodging | 7949 | 4992 | 6177 | 7225 | 6710 | 7516 | 6709 | 7860 | 6585 |  | Restaurant | ETDFw | 0.0001305 | 0 | 0 | 0 | 0
Health - Other | 200 | 95.4% | 95% | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% | 200 | 96.2% | 95.8% | 95.8% | 95.4% | 94.5% | 94.1% | CHWP | Office | 2433 | 1388 | 1653 | 2203 | 2002 | 2484 | 2052 | 2277 | 1951 |  | Retail | ETDFs | 0.000177 | 0.000472 | 0.0002762 | 0.0001031 | 0.000472 | Tables 3-95 and 3-96: Power Part Load Ratios
Industrial Manufacturing | 250 | 95.8% | 95% | 96.2% | 95.8% | 95.8% | 95.8% | 95% | 95% | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | CHWP | Restaurant | [10 empty] | Retail | ETDFw | 0.000118 | 1.19e-05 | 1.3e-05 | 9.45e-05 | 1.19e-05 | Flow Fraction (%) | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
Institutional/Public Service | 300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | CHWP | Retail | 4022 | 2392 | 2797 | 3688 | 3424 | 3935 | 3298 | 3802 | 3304 |  | Warehouse - Other | ETDFs | 0.000195 | 0 | 0 | 0 | 0 | Fan: VFD | 0.0475 | 0.0475 | 0.0537 | 0.08 | 0.1289 | 0.2027 | 0.3038 | 0.4346 | 0.5975 | 0.795 | 1.0293
Lodging | 350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | CHWP | Warehouse - Other | [10 empty] | Warehouse - Other | ETDFw | 0.0001268 | 0 | 0 | 0 | 0 | Pump: VFD | 0.27448 | 0.19124 | 0.14325 | 0.1305 | 0.15298 | 0.21071 | 0.30368 | 0.43188 | 0.59533 | 0.79402 | 1.0279
Office | 400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A | N/A | [7 empty] | CHWP | Warehouse - Refrigerated | [10 empty] | Warehouse - Refrigerated | ETDFs | 0.000195 | 0 | 0 | 0 | 0 | Fan: Forward Curved with Inlet Guide Vanes | 0.2 | 0.20643 | 0.2157 | 0.2332 | 0.26435 | 0.31454 | 0.38917 | 0.49364 | 0.63334 | 0.81369 | 1.0401
Restaurant | 450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CTF | Education - College/University | 5448 | 3401 | 4303 | 5061 | 4503 | 5257 | 4619 | 5320 | 4413 | 0.76 | Warehouse - Refrigerated | ETDFw | 0.0001268 | 0 | 0 | 0 | 0 | Fan: Air Foil / Backward Incline with Inlet Guide Vanes | 0.47262 | 0.52642 | 0.55755 | 0.57439 | 0.58535 | 0.59884 | 0.62324 | 0.66697 | 0.73841 | 0.84597 | 0.99806
Retail | 500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CTF | Education - Other | 3729 | 1832 | 2271 | 3027 | 3046 | 4291 | 3168 | 3215 | 2969 | 0.76 | [7 empty] | Fan: Two-Speed CT Fan | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1
Warehouse - Other | Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CTF | Grocery | [17 empty] | Fan: Forward Curved | 0.20419 | 0.22262 | 0.25596 | 0.30419 | 0.36732 | 0.44536 | 0.53829 | 0.64612 | 0.76885 | 0.90649 | 1.059
Warehouse - Refrigerated | Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CTF | Health - Hospital | 7598 | 4750 | 5789 | 7099 | 6343 | 7422 | 6597 | 7316 | 6414 | [8 empty] | Fan: Air Foil / Backward Incline | 0.53 | 0.5256 | 0.53276 | 0.57235 | 0.63599 | 0.71526 | 0.80178 | 0.88713 | 0.96293 | 1.0208 | 1.0522
| Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CTF | Health - Other | 5296 | 3062 | 3604 | 4805 | 4558 | 5535 | 4604 | 5158 | 4354 | [8 empty] | Fan: Constant Volume | bar: 0% to 100%
NEMA Design Types | [16 empty] | CTF | Industrial Manufacturing | 2360 | 1293 | 1510 | 2013 | 1934 | 2307 | 1895 | 2166 | 1862 | [8 empty] | Pump: Throttle Valve | 0.55212 | 0.61392 | 0.67192 | 0.72612 | 0.77652 | 0.82312 | 0.86592 | 0.90492 | 0.94012 | 0.97152 | 0.99912
NEMA Design A | [16 empty] | CTF | Institutional/Public Service | [17 empty] | Pump: Constant Volume | bar: 0% to 100%
NEMA Design B | Table 3‑84/85: Baseline Efficiencies for NEMA Design A and NEMA Design B Motors | [15 empty] | CTF | Lodging | 7948 | 4989 | 6174 | 7224 | 6708 | 7514 | 6706 | 7856 | 6581
NEMA Design C | HP | 2 Pole (3600 RPM) |  | 4 Pole (1800 RPM) |  | 6 Pole (1200 RPM) |  | 8 Pole (900 RPM) | [8 empty] | CTF | Office | 2433 | 1388 | 1653 | 2203 | 2002 | 2484 | 2052 | 2277 | 1951
|  | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | [7 empty] | CTF | Restaurant
City |  | TEFC2 | ODP2 | TEFC4 | ODP4 | TEFC6 | ODP6 | TEFC8 | ODP8 | [7 empty] | CTF | Retail | 4022 | 2392 | 2797 | 3688 | 3424 | 3936 | 3298 | 3803 | 3304
Allentown | 1 | 77% | 77% | 85.5% | 85.5% | 82.5% | 82% | 75.5% | 75.5% | [7 empty] | CTF | Warehouse - Other
Binghamton | 1.5 | 84% | 84% | 86.5% | 86.5% | 87.5% | 86.5% | 78.5% | 77% | [7 empty] | CTF | Warehouse - Refrigerated
Bradford | 2 | 85.5% | 85.5% | 86.5% | 86.5% | 88.5% | 87.5% | 84% | 86.5% | [7 empty] | HHWP | Education - College/University | 4548 | 5271 | 5900 | 5036 | 4250 | 4014 | 4572 | 4638 | 4487 | 0.79
Erie | 3 | 86.5% | 85.5% | 89.5% | 89.5% | 89.5% | 88.5% | 85.5% | 87.5% | [7 empty] | HHWP | Education - Other | 3651 | 4251 | 4722 | 4080 | 3492 | 3341 | 3705 | 3830 | 3658
Harrisburg | 5 | 88.5% | 86.5% | 89.5% | 89.5% | 89.5% | 89.5% | 86.5% | 88.5% | [7 empty] | HHWP | Grocery
Philadelphia | 7.5 | 89.5% | 88.5% | 91.7% | 91% | 91% | 90.2% | 86.5% | 89.5% | [7 empty] | HHWP | Health - Hospital | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Pittsburgh | 10 | 90.2% | 89.5% | 91.7% | 91.7% | 91% | 91.7% | 89.5% | 90.2% | [7 empty] | HHWP | Health - Other | 5934 | 6627 | 7170 | 6280 | 5823 | 5477 | 5991 | 6223 | 6045
Scranton | 15 | 91% | 90.2% | 92.4% | 93% | 91.7% | 91.7% | 89.5% | 90.2% | [7 empty] | HHWP | Industrial Manufacturing | 1258 | 1684 | 1944 | 1555 | 1184 | 1028 | 1287 | 1393 | 1277
Williamsport | 20 | 91% | 91% | 93% | 93% | 91.7% | 92.4% | 90.2% | 91% | [7 empty] | HHWP | Institutional/Public Service
| 25 | 91.7% | 91.7% | 93.6% | 93.6% | 93% | 93% | 90.2% | 91% | [7 empty] | HHWP | Lodging | 6469 | 7072 | 7587 | 6829 | 6155 | 6077 | 6574 | 6628 | 6387
Program Year | 30 | 91.7% | 91.7% | 93.6% | 94.1% | 93% | 93.6% | 91.7% | 91.7% | [7 empty] | HHWP | Office | 3214 | 3876 | 4446 | 3611 | 3014 | 2690 | 3246 | 3336 | 3169
PY18 | 40 | 92.4% | 92.4% | 94.1% | 94.1% | 94.1% | 94.1% | 91.7% | 91.7% | [7 empty] | HHWP | Restaurant
PY19 | 50 | 93% | 93% | 94.5% | 94.5% | 94.1% | 94.1% | 92.4% | 92.4% | [7 empty] | HHWP | Retail | 2676 | 3183 | 3568 | 2960 | 2561 | 2398 | 2908 | 2841 | 2660
PY20 | 60 | 93.6% | 93.6% | 95% | 95% | 94.5% | 94.5% | 92.4% | 93% | [7 empty] | HHWP | Warehouse - Other
PY21 | 75 | 93.6% | 93.6% | 95.4% | 95% | 94.5% | 94.5% | 93.6% | 94.1% | [7 empty] | HHWP | Warehouse - Refrigerated
PY22 | 100 | 95% | 94.5% | 96.2% | 96.2% | 95.8% | 95.8% | 94.5% | 95% | [7 empty] | CW Pump | Education - College/University | 4797 | 2909 | 3428 | 4258 | 3998 | 4917 | 4424 | 4865 | 3977 | 0.79
| 125 | 95.4% | 94.5% | 96.2% | 96.2% | 95.8% | 95.8% | 95% | 95% | [7 empty] | CW Pump | Education - Other | 3329 | 1716 | 2125 | 2834 | 2818 | 4082 | 2843 | 3008 | 2762
| 150 | 95.4% | 94.5% | 96.2% | 96.2% | 96.2% | 95.8% | 95% | 95% | [7 empty] | CW Pump | Grocery
| 200 | 95.8% | 95.4% | 96.5% | 96.2% | 96.2% | 95.8% | 95.4% | 95% | [7 empty] | CW Pump | Health - Hospital | 5372 | 3511 | 4577 | 5140 | 4093 | 5085 | 4830 | 5161 | 4184
| 250 | 96.2% | 95.4% | 96.5% | 96.2% | 96.2% | 96.2% | 95.4% | 95.4% | [7 empty] | CW Pump | Health - Other | 4998 | 3069 | 3593 | 4718 | 4135 | 5251 | 4214 | 5125 | 4243
| 300 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | [7 empty] | CW Pump | Industrial Manufacturing | 2360 | 1292 | 1507 | 2009 | 1928 | 2305 | 1890 | 2166 | 1860
| 350 | 95.8% | 95.4% | 96.2% | 95.8% | 95.8% | 95.8% | N/A | N/A | [7 empty] | CW Pump | Institutional/Public Service
| 400 | 95.8% | 95.8% | 96.2% | 95.8% | N/A | N/A | N/A | N/A | [7 empty] | CW Pump | Lodging | 7540 | 4545 | 5475 | 6625 | 6182 | 7181 | 6182 | 7441 | 6074
| 450 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CW Pump | Office | 2422 | 1375 | 1636 | 2181 | 1989 | 2473 | 2041 | 2267 | 1940
| 500 | 95.8% | 96.2% | 96.2% | 96.2% | N/A | N/A | N/A | N/A | [7 empty] | CW Pump | Restaurant
| Custom 1 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CW Pump | Retail | 3929 | 2357 | 2761 | 3636 | 3358 | 3886 | 3253 | 3756 | 3246
| Custom 2 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CW Pump | Warehouse - Other
| Custom 3 | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | [7 empty] | CW Pump | Warehouse - Refrigerated

## Changelog
Pennsylvania Act 129 Motors and Drives Audit and Design Tool
CHANGELOG
Version 7 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 8 (Submitted October 27, 2011. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
Version 9 (Submitted September 13, 2011 for 2012 TRM Tentative Order)
1) | In "Motor and VFD Form", revised formulas in Columns O, P, and S to correct referencing errors
2) | In "Motor and VFD Form", added Column Q (Full Load kW) to correct a calculation error incorrectly applying DSF
3) | In "Motor and VFD Form", revised Column G (Coincidence Factor) to reflect TRM values (0.74 for single, 0.37 for duplex)
4) | In "Glossary", revised definition of coincidence factor to reflect above change.
5) | In "Glossary", added definition for "Full Load kW"
6) | In "Glossary", revised definition of "Nominal Efficiency" to reflect ability to custom input efficiency values for the new motor efficiency and baseline motor efficiency if the new motor is for new construction or replace on burnout.
7) | In "Manual", updated TRM reference from Table 6-12 to Table 3-15
Version 10 (Submitted December 5, 2011 for 2012 TRM Final Order)
1) | In "Motor and VFD Form", updated operating hours lookup table to reflect TRM table.
2) | In "Motor and VFD Form", corrected formulas for efficiency lookups, post-installation peak kW calculation, and total kWh calculation for post-installation line item #7.
3) | In "Motor and VFD Form", updated form to include new ESF and DSF values.
4) | In "Glossary", updated entries to reflect new column O and definition of "baseline".
Version 11 (Submitted August 31, 2012 for 2013 TRM Tentative Order)
1) | Created "Motor Form" and "VFD Form" to calculate savings for motors and VFD measures separately to be consistent with TRM protocols.
2) | In "Motor Form" and "VFD Form", updated operating hours lookup table to reflect TRM table.
3) | In "VFD Form", updated ESF and DSF values lookup table to reflect TRM table.
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D
Version 12 (Submitted December 07, 2012 for 2013 TRM Final Order)
1) | Changed the definition of "Load Factor" in Glossary to be consistent with TRM protocols.
Version 13 (Submitted August 29, 2013 for 2014 TRM Tentative Order)
1) | Revised the algorithms in Column R of the "VFD Form" tab used to calculate energy and peak demand savings to be consistent with TRM protocols. Removed a conversion factor of 0.746 to convert from HP to kW.
Version 13 (Submitted December 05, 2013 for 2014 TRM Final Order)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed motor efficiency tables from "VFD Form".
3) | Revised "Motor Form" and added "Motor Custom Input" to allow for addition of custom motor applications.
4) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
Version 14 (Submitted August 05, 2014)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Updated "Coincidence Factor" , "Operating Hours" and "Facility Type" lookup tables to reflect new changes to the TRM.
3) | Formulas for Coincidence Factor and Operating hours are updated to reflect changes to the TRM.
4) | Consolidated all lookup tables under single tab "Lookup Tables"; updated references to lookup tables.
5) | Added "City" to the general information section for "Motor Form" , "VFD Form" , "Motor Custom Input" and "Summary"
6) | Linked general information cells of "Motor Form" , "VFD Form" and "Motor Custom Input" to cells in "Summary". Locked the cells to protect their links.
7) | Motor Configuration column is deleted from "Motor Form" and "VFD Form"
8) | Installation date cell is modified to allow entry of a date between 6/1/2015 and 5/31/2016 only. For all other dates , an error message is displayed.
9) | Program Year is limited to Program Year 7.
10) | "VFD on Motor" column is deleted from "VFD Form". The formulas for ESF, DSF and Full Load kW are updated to exclude the deleted column.
11) | "Full Load kW" on "VFD Form" revised - previously displayed a horsepower value. "Peak kW" and "Annual kWh" adjusted to account for change made to "Full Load kW."
12) | Introduced a macro button on "Motor Form" and "VFD Form" that increases number of motor line items for user's convenience.
13) | Added 900 RPM option to "Synchronous Speed" for "Motor Form", "VFD Form" and "Motor Custom Form."
14) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D.
15) | References to "Hot Water Pump" changed to "Heating Hot Water Pump" to be consistent with TRM. References to "HWP" changed to "HHWP."
Version 15 (Submitted February 20, 2015)
1) | Updated motor efficiency tables to reflect new changes to the TRM.
2) | Removed "Nema Design Type", "Synchronous Speed" and "Enclosure Type" fields from post-installation data in "Motor Form"
Version 16 (Submitted June 1, 2015)
1) Relocated "Summary" form before the other input forms
2) Updated selectable program years to reflect Phase III program years
3) Updated TRM table references in "Lookup Tables"
Version 17 (Submitted June 1, 2015)
1) Major revisions to the 'VFD Form' tab:
1.1) Renamed to '3.3.2 VFD Improvements'
1.2) Algorithms changed to reflect 2021 TRM. Instead of defined ESF/DSFs, new algorithm uses load profiles, and baseline and VFD part load factors.
1.3) Capability to define custom load profiles added. (See 'VFD Custom Load Profile' tab.) Default 'HVAC Fan' and 'HVAC Pump' profiles included.
2) Reformatted 'Motor Form' to align with new 'VFD Inventory' format, including name change to '3.3.1 Premium Efficiency Motors'
3) 'General Information' tab created to house basic project information.
Version 18 (Submitted May 2024 for 2026 TRM Tentative Order)
1) Major revisions and modifications to worksheet "Lookup" tables
1.1) Annual Run Hours table revised to reflect updated values
1.2) ETDF Table Added
1.3) Two (2) VFD Flow Fraction options added to "Tables 3-74 and 3-75: Power Part Load Ratios"
1.3a) Revision to "Fan: Air Foil / Backward Incline" value at 0%, from 0.56 to 0.53
1.4) Added Program Year lookup list to column A
1.5) Added new lookup table (NEMA_Design_A_or_B_2027) to provide updated baseline efficiency
1.6) Removal of unused lists
1.6a) Baseline Control Types
1.6b) Default Load Profile & VFD Control Type in Motor Function Table
2) Minor revisions to worksheet 3.3.1 Premium Efficiency Motors
2.1) Default Annual Run Hours MATCH function change to accommodate Lookup worksheet table modifications
2.2) Added Program Year input allowing for updated PY19 NEMA Design A and B motor efficiencies per federal standards
2.3) ETDF Implementation
2.3a) Columns and formulas added to lookup summer and winter ETDF values
2.3b) Summer and winter peak demand savings calculations with ETDF additions
2.3c) Removal of coincident factors
3) 3.3.2 VFD Improvements
3.1) Default Load Factor (LF) LOOKUP function change to accommodate Lookup worksheet table modifications
3.2) Default Annual Run Hours MATCH function change to accommodate Lookup worksheet table modifications
3.3) Column N (Power Part Load Ratio) drop menu added into the post-retrofit details inputs
3.2a) This was necessary since there are now multiple power part load ratio curves for fans
3.4) "Summer" and "Winter" peak demand savings separated into columns BH and BI respectively
3.4a) Necessitated the division of Energy Efficient Peak Demand into "Summer" and "Winter" columns BE and BF respectively
3.4b) Necessitated the division of Average Flow Fraction During Peak into "Summer" and "Winter" columns O and P respectively
4) VFD Custom Load Profile worksheet updates
4.1) Revised HVAC Fan load profile flow fraction values to align with TRM
4.2) Default HVAC Fan load profile linked to values in the Lookup worksheet
4.3) Default HVAC Pump load profile linked to values in the Lookup worksheet
Version 19 (Submitted Septmber 2024 for 2026 TRM Tentative Order)
1) Corrected Look-up Table Numbers to align with the 2026 TRM
2) Corrected formula lookup errors on sheet 3.3.1 for Load Factor and Run Hours